## Kota
Date | Daywise mean temperature | Running mean temperature (RMT) | Neutral temperature_IMAC | Baseline temperature calculated from PMV model | Plant adjusted I (Baseline + 0.5°C) | Plant adjusted II (Baseline + 1°C) | Plant adjusted I+ IMAC | Plant adjusted II+ IMAC | ACDD based on IMAC neutral temperature | 1014.0791 | ACDD based on baseline temperature i.e. 24.5 calculated from the PMV model | 1442.3 | ACDD based on 0.5°C adjustment on baseline temperature because of plant | 1322.9708 | ACDD based on 1°C adjustment on baseline temperature because of plant | 1209.1417 | ACDD based on IMAC neutral temperature considering 0.5°C plant effect | 898.2832 | ACDD based on IMAC neutral temperature considering 1°C plant effect | 789.1
1990-01-01 | 17.7708 | 18.356 | 23.0097 | 24.5 | 25 | 25.5 | 23.5097 | 24.0097 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-02 | 15.4833 | 18.3347 | 23.0037 | 24.5 | 25 | 25.5 | 23.5037 | 24.0037 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-03 | 15.0792 | 18.2025 | 22.9667 | 24.5 | 25 | 25.5 | 23.4667 | 23.9667 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-04 | 15.05 | 18.0571 | 22.926 | 24.5 | 25 | 25.5 | 23.426 | 23.926 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-05 | 16.1917 | 17.9061 | 22.8837 | 24.5 | 25 | 25.5 | 23.3837 | 23.8837 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-06 | 17.8792 | 17.7904 | 22.8513 | 24.5 | 25 | 25.5 | 23.3513 | 23.8513 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-07 | 18.7792 | 17.7913 | 22.8516 | 24.5 | 25 | 25.5 | 23.3516 | 23.8516 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-08 | 18.1833 | 17.8365 | 22.8642 | 24.5 | 25 | 25.5 | 23.3642 | 23.8642 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-09 | 18.075 | 17.8672 | 22.8728 | 24.5 | 25 | 25.5 | 23.3728 | 23.8728 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-10 | 14.7167 | 17.8819 | 22.8769 | 24.5 | 25 | 25.5 | 23.3769 | 23.8769 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-11 | 15.2375 | 17.7957 | 22.8528 | 24.5 | 25 | 25.5 | 23.3528 | 23.8528 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-12 | 14.6458 | 17.7147 | 22.8301 | 24.5 | 25 | 25.5 | 23.3301 | 23.8301 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-13 | 14.2333 | 17.5854 | 22.7939 | 24.5 | 25 | 25.5 | 23.2939 | 23.7939 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-14 | 13.9917 | 17.4614 | 22.7592 | 24.5 | 25 | 25.5 | 23.2592 | 23.7592 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-15 | 14.8083 | 17.3329 | 22.7232 | 24.5 | 25 | 25.5 | 23.2232 | 23.7232 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-16 | 15.4833 | 17.2214 | 22.692 | 24.5 | 25 | 25.5 | 23.192 | 23.692 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-17 | 16.2708 | 17.1372 | 22.6684 | 24.5 | 25 | 25.5 | 23.1684 | 23.6684 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-18 | 16.3 | 17.0767 | 22.6515 | 24.5 | 25 | 25.5 | 23.1515 | 23.6515 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-19 | 16.7208 | 16.9946 | 22.6285 | 24.5 | 25 | 25.5 | 23.1285 | 23.6285 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-20 | 15.4333 | 16.9893 | 22.627 | 24.5 | 25 | 25.5 | 23.127 | 23.627 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-21 | 15.8542 | 16.9465 | 22.615 | 24.5 | 25 | 25.5 | 23.115 | 23.615 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-22 | 16.45 | 16.8967 | 22.6011 | 24.5 | 25 | 25.5 | 23.1011 | 23.6011 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-23 | 17.9583 | 16.8504 | 22.5881 | 24.5 | 25 | 25.5 | 23.0881 | 23.5881 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-24 | 18.6917 | 16.8517 | 22.5885 | 24.5 | 25 | 25.5 | 23.0885 | 23.5885 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-25 | 19.05 | 16.8492 | 22.5878 | 24.5 | 25 | 25.5 | 23.0878 | 23.5878 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-26 | 19.3333 | 16.9031 | 22.6029 | 24.5 | 25 | 25.5 | 23.1029 | 23.6029 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-27 | 20.7708 | 16.9364 | 22.6122 | 24.5 | 25 | 25.5 | 23.1122 | 23.6122 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-28 | 20.9708 | 16.9454 | 22.6147 | 24.5 | 25 | 25.5 | 23.1147 | 23.6147 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-29 | 20.1833 | 16.9572 | 22.618 | 24.5 | 25 | 25.5 | 23.118 | 23.618 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-30 | 18.7083 | 16.9826 | 22.6251 | 24.5 | 25 | 25.5 | 23.1251 | 23.6251 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-31 | 16.5792 | 16.9435 | 22.6142 | 24.5 | 25 | 25.5 | 23.1142 | 23.6142 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-01 | 15.3792 | 16.9037 | 22.603 | 24.5 | 25 | 25.5 | 23.103 | 23.603 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-02 | 14.8667 | 16.9003 | 22.6021 | 24.5 | 25 | 25.5 | 23.1021 | 23.6021 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-03 | 14.7042 | 16.8932 | 22.6001 | 24.5 | 25 | 25.5 | 23.1001 | 23.6001 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-04 | 14.7083 | 16.8817 | 22.5969 | 24.5 | 25 | 25.5 | 23.0969 | 23.5969 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-05 | 15.0208 | 16.8322 | 22.583 | 24.5 | 25 | 25.5 | 23.083 | 23.583 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-06 | 15.375 | 16.7369 | 22.5563 | 24.5 | 25 | 25.5 | 23.0563 | 23.5563 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-07 | 16.3083 | 16.6235 | 22.5246 | 24.5 | 25 | 25.5 | 23.0246 | 23.5246 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-08 | 16.125 | 16.561 | 22.5071 | 24.5 | 25 | 25.5 | 23.0071 | 23.5071 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-09 | 16.1833 | 16.496 | 22.4889 | 24.5 | 25 | 25.5 | 22.9889 | 23.4889 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-10 | 16.5667 | 16.5449 | 22.5026 | 24.5 | 25 | 25.5 | 23.0026 | 23.5026 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-11 | 17.2625 | 16.5892 | 22.515 | 24.5 | 25 | 25.5 | 23.015 | 23.515 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-12 | 18.2292 | 16.6764 | 22.5394 | 24.5 | 25 | 25.5 | 23.0394 | 23.5394 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-13 | 19.3458 | 16.8096 | 22.5767 | 24.5 | 25 | 25.5 | 23.0767 | 23.5767 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-14 | 20.5167 | 16.9881 | 22.6267 | 24.5 | 25 | 25.5 | 23.1267 | 23.6267 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-15 | 21.1833 | 17.1783 | 22.6799 | 24.5 | 25 | 25.5 | 23.1799 | 23.6799 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-16 | 21.3167 | 17.3683 | 22.7331 | 24.5 | 25 | 25.5 | 23.2331 | 23.7331 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-17 | 20.7042 | 17.5365 | 22.7802 | 24.5 | 25 | 25.5 | 23.2802 | 23.7802 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-18 | 21.5083 | 17.6833 | 22.8213 | 24.5 | 25 | 25.5 | 23.3213 | 23.8213 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-19 | 20.8458 | 17.8429 | 22.866 | 24.5 | 25 | 25.5 | 23.366 | 23.866 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-20 | 22.6917 | 18.0233 | 22.9165 | 24.5 | 25 | 25.5 | 23.4165 | 23.9165 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-21 | 22.9625 | 18.2512 | 22.9804 | 24.5 | 25 | 25.5 | 23.4804 | 23.9804 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-22 | 23.3583 | 18.4683 | 23.0411 | 24.5 | 25 | 25.5 | 23.5411 | 24.0411 | 0.3172 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-23 | 24.3083 | 18.6483 | 23.0915 | 24.5 | 25 | 25.5 | 23.5915 | 24.0915 | 1.2168 |  | 0 |  | 0 |  | 0 |  | 0.7168 |  | 0.2168
1990-02-24 | 23.8 | 18.8356 | 23.144 | 24.5 | 25 | 25.5 | 23.644 | 24.144 | 0.65604 |  | 0 |  | 0 |  | 0 |  | 0.15604 |  | 0
1990-02-25 | 22.6375 | 18.9939 | 23.1883 | 24.5 | 25 | 25.5 | 23.6883 | 24.1883 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-26 | 20.6625 | 19.104 | 23.2191 | 24.5 | 25 | 25.5 | 23.7191 | 24.2191 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-27 | 21.2958 | 19.1004 | 23.2181 | 24.5 | 25 | 25.5 | 23.7181 | 24.2181 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-28 | 23.425 | 19.1112 | 23.2212 | 24.5 | 25 | 25.5 | 23.7212 | 24.2212 | 0.20385 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-01 | 24.4375 | 19.2193 | 23.2514 | 24.5 | 25 | 25.5 | 23.7514 | 24.2514 | 1.1861 |  | 0 |  | 0 |  | 0 |  | 0.68609 |  | 0.18609
1990-03-02 | 23.7667 | 19.4103 | 23.3049 | 24.5 | 25 | 25.5 | 23.8049 | 24.3049 | 0.46179 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-03 | 23.8 | 19.6499 | 23.372 | 24.5 | 25 | 25.5 | 23.872 | 24.372 | 0.42804 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-04 | 25.6625 | 19.9306 | 23.4506 | 24.5 | 25 | 25.5 | 23.9506 | 24.4506 | 2.2119 |  | 1.1625 |  | 0.6625 |  | 0.1625 |  | 1.7119 |  | 1.2119
1990-03-05 | 26.4875 | 20.2904 | 23.5513 | 24.5 | 25 | 25.5 | 24.0513 | 24.5513 | 2.9362 |  | 1.9875 |  | 1.4875 |  | 0.9875 |  | 2.4362 |  | 1.9362
1990-03-06 | 27.3708 | 20.6832 | 23.6613 | 24.5 | 25 | 25.5 | 24.1613 | 24.6613 | 3.7095 |  | 2.8708 |  | 2.3708 |  | 1.8708 |  | 3.2095 |  | 2.7095
1990-03-07 | 25.9292 | 21.1053 | 23.7795 | 24.5 | 25 | 25.5 | 24.2795 | 24.7795 | 2.1497 |  | 1.4292 |  | 0.92917 |  | 0.42917 |  | 1.6497 |  | 1.1497
1990-03-08 | 25.1 | 21.4689 | 23.8813 | 24.5 | 25 | 25.5 | 24.3813 | 24.8813 | 1.2187 |  | 0.6 |  | 0.1 |  | 0 |  | 0.71871 |  | 0.21871
1990-03-09 | 24.5583 | 21.7931 | 23.9721 | 24.5 | 25 | 25.5 | 24.4721 | 24.9721 | 0.58628 |  | 0.058333 |  | 0 |  | 0 |  | 0.086278 |  | 0
1990-03-10 | 25.8083 | 22.0681 | 24.0491 | 24.5 | 25 | 25.5 | 24.5491 | 25.0491 | 1.7593 |  | 1.3083 |  | 0.80833 |  | 0.30833 |  | 1.2593 |  | 0.75928
1990-03-11 | 24.0208 | 22.3908 | 24.1394 | 24.5 | 25 | 25.5 | 24.6394 | 25.1394 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-12 | 24.9333 | 22.6521 | 24.2126 | 24.5 | 25 | 25.5 | 24.7126 | 25.2126 | 0.72075 |  | 0.43333 |  | 0 |  | 0 |  | 0.22075 |  | 0
1990-03-13 | 24.3667 | 22.931 | 24.2907 | 24.5 | 25 | 25.5 | 24.7907 | 25.2907 | 0.075994 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-14 | 23.3958 | 23.1678 | 24.357 | 24.5 | 25 | 25.5 | 24.857 | 25.357 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-15 | 21.7 | 23.34 | 24.4052 | 24.5 | 25 | 25.5 | 24.9052 | 25.4052 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-16 | 23.3208 | 23.4185 | 24.4272 | 24.5 | 25 | 25.5 | 24.9272 | 25.4272 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-17 | 24.5583 | 23.5119 | 24.4533 | 24.5 | 25 | 25.5 | 24.9533 | 25.4533 | 0.10499 |  | 0.058333 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-18 | 25.2708 | 23.6244 | 24.4848 | 24.5 | 25 | 25.5 | 24.9848 | 25.4848 | 0.78599 |  | 0.77083 |  | 0.27083 |  | 0 |  | 0.28599 |  | 0
1990-03-19 | 23.9292 | 23.7562 | 24.5217 | 24.5 | 25 | 25.5 | 25.0217 | 25.5217 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-20 | 23.5875 | 23.8637 | 24.5518 | 24.5 | 25 | 25.5 | 25.0518 | 25.5518 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-21 | 23.8458 | 23.9331 | 24.5713 | 24.5 | 25 | 25.5 | 25.0713 | 25.5713 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-22 | 24.9833 | 24.0331 | 24.5993 | 24.5 | 25 | 25.5 | 25.0993 | 25.5993 | 0.38408 |  | 0.48333 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-23 | 22.6708 | 24.1094 | 24.6206 | 24.5 | 25 | 25.5 | 25.1206 | 25.6206 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-24 | 24.2625 | 24.0997 | 24.6179 | 24.5 | 25 | 25.5 | 25.1179 | 25.6179 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-25 | 26.6917 | 24.1299 | 24.6264 | 24.5 | 25 | 25.5 | 25.1264 | 25.6264 | 2.0653 |  | 2.1917 |  | 1.6917 |  | 1.1917 |  | 1.5653 |  | 1.0653
1990-03-26 | 28.0542 | 24.2093 | 24.6486 | 24.5 | 25 | 25.5 | 25.1486 | 25.6486 | 3.4056 |  | 3.5542 |  | 3.0542 |  | 2.5542 |  | 2.9056 |  | 2.4056
1990-03-27 | 28.625 | 24.3511 | 24.6883 | 24.5 | 25 | 25.5 | 25.1883 | 25.6883 | 3.9367 |  | 4.125 |  | 3.625 |  | 3.125 |  | 3.4367 |  | 2.9367
1990-03-28 | 30.5917 | 24.5507 | 24.7442 | 24.5 | 25 | 25.5 | 25.2442 | 25.7442 | 5.8475 |  | 6.0917 |  | 5.5917 |  | 5.0917 |  | 5.3475 |  | 4.8475
1990-03-29 | 31.9042 | 24.8817 | 24.8369 | 24.5 | 25 | 25.5 | 25.3369 | 25.8369 | 7.0673 |  | 7.4042 |  | 6.9042 |  | 6.4042 |  | 6.5673 |  | 6.0673
1990-03-30 | 31.65 | 25.2353 | 24.9359 | 24.5 | 25 | 25.5 | 25.4359 | 25.9359 | 6.7141 |  | 7.15 |  | 6.65 |  | 6.15 |  | 6.2141 |  | 5.7141
1990-03-31 | 30.9875 | 25.5094 | 25.0126 | 24.5 | 25 | 25.5 | 25.5126 | 26.0126 | 5.9749 |  | 6.4875 |  | 5.9875 |  | 5.4875 |  | 5.4749 |  | 4.9749
1990-04-01 | 28.1625 | 25.7278 | 25.0738 | 24.5 | 25 | 25.5 | 25.5738 | 26.0738 | 3.0887 |  | 3.6625 |  | 3.1625 |  | 2.6625 |  | 2.5887 |  | 2.0887
1990-04-02 | 29.6375 | 25.8743 | 25.1148 | 24.5 | 25 | 25.5 | 25.6148 | 26.1148 | 4.5227 |  | 5.1375 |  | 4.6375 |  | 4.1375 |  | 4.0227 |  | 3.5227
1990-04-03 | 27.2583 | 26.0689 | 25.1693 | 24.5 | 25 | 25.5 | 25.6693 | 26.1693 | 2.089 |  | 2.7583 |  | 2.2583 |  | 1.7583 |  | 1.589 |  | 1.089
1990-04-04 | 26.9208 | 26.1221 | 25.1842 | 24.5 | 25 | 25.5 | 25.6842 | 26.1842 | 1.7366 |  | 2.4208 |  | 1.9208 |  | 1.4208 |  | 1.2366 |  | 0.73665
1990-04-05 | 29.3917 | 26.1365 | 25.1882 | 24.5 | 25 | 25.5 | 25.6882 | 26.1882 | 4.2034 |  | 4.8917 |  | 4.3917 |  | 3.8917 |  | 3.7034 |  | 3.2034
1990-04-06 | 28.6542 | 26.2039 | 25.2071 | 24.5 | 25 | 25.5 | 25.7071 | 26.2071 | 3.4471 |  | 4.1542 |  | 3.6542 |  | 3.1542 |  | 2.9471 |  | 2.4471
1990-04-07 | 30.0292 | 26.2947 | 25.2325 | 24.5 | 25 | 25.5 | 25.7325 | 26.2325 | 4.7966 |  | 5.5292 |  | 5.0292 |  | 4.5292 |  | 4.2966 |  | 3.7966
1990-04-08 | 31.5875 | 26.459 | 25.2785 | 24.5 | 25 | 25.5 | 25.7785 | 26.2785 | 6.309 |  | 7.0875 |  | 6.5875 |  | 6.0875 |  | 5.809 |  | 5.309
1990-04-09 | 32.8958 | 26.6933 | 25.3441 | 24.5 | 25 | 25.5 | 25.8441 | 26.3441 | 7.5517 |  | 8.3958 |  | 7.8958 |  | 7.3958 |  | 7.0517 |  | 6.5517
1990-04-10 | 32.6083 | 26.9296 | 25.4103 | 24.5 | 25 | 25.5 | 25.9103 | 26.4103 | 7.198 |  | 8.1083 |  | 7.6083 |  | 7.1083 |  | 6.698 |  | 6.198
1990-04-11 | 33.0375 | 27.2158 | 25.4904 | 24.5 | 25 | 25.5 | 25.9904 | 26.4904 | 7.5471 |  | 8.5375 |  | 8.0375 |  | 7.5375 |  | 7.0471 |  | 6.5471
1990-04-12 | 33.4 | 27.486 | 25.5661 | 24.5 | 25 | 25.5 | 26.0661 | 26.5661 | 7.8339 |  | 8.9 |  | 8.4 |  | 7.9 |  | 7.3339 |  | 6.8339
1990-04-13 | 33.8333 | 27.7871 | 25.6504 | 24.5 | 25 | 25.5 | 26.1504 | 26.6504 | 8.1829 |  | 9.3333 |  | 8.8333 |  | 8.3333 |  | 7.6829 |  | 7.1829
1990-04-14 | 34.2792 | 28.135 | 25.7478 | 24.5 | 25 | 25.5 | 26.2478 | 26.7478 | 8.5314 |  | 9.7792 |  | 9.2792 |  | 8.7792 |  | 8.0314 |  | 7.5314
1990-04-15 | 35.0542 | 28.5543 | 25.8652 | 24.5 | 25 | 25.5 | 26.3652 | 26.8652 | 9.189 |  | 10.5542 |  | 10.0542 |  | 9.5542 |  | 8.689 |  | 8.189
1990-04-16 | 35.7375 | 28.9454 | 25.9747 | 24.5 | 25 | 25.5 | 26.4747 | 26.9747 | 9.7628 |  | 11.2375 |  | 10.7375 |  | 10.2375 |  | 9.2628 |  | 8.7628
1990-04-17 | 35.625 | 29.3181 | 26.0791 | 24.5 | 25 | 25.5 | 26.5791 | 27.0791 | 9.5459 |  | 11.125 |  | 10.625 |  | 10.125 |  | 9.0459 |  | 8.5459
1990-04-18 | 33.8792 | 29.6632 | 26.1757 | 24.5 | 25 | 25.5 | 26.6757 | 27.1757 | 7.7035 |  | 9.3792 |  | 8.8792 |  | 8.3792 |  | 7.2035 |  | 6.7035
1990-04-19 | 32.4958 | 29.9949 | 26.2686 | 24.5 | 25 | 25.5 | 26.7686 | 27.2686 | 6.2273 |  | 7.9958 |  | 7.4958 |  | 6.9958 |  | 5.7273 |  | 5.2273
1990-04-20 | 32.8 | 30.2918 | 26.3517 | 24.5 | 25 | 25.5 | 26.8517 | 27.3517 | 6.4483 |  | 8.3 |  | 7.8 |  | 7.3 |  | 5.9483 |  | 5.4483
1990-04-21 | 33.2917 | 30.5903 | 26.4353 | 24.5 | 25 | 25.5 | 26.9353 | 27.4353 | 6.8564 |  | 8.7917 |  | 8.2917 |  | 7.7917 |  | 6.3564 |  | 5.8564
1990-04-22 | 33.2208 | 30.8672 | 26.5128 | 24.5 | 25 | 25.5 | 27.0128 | 27.5128 | 6.708 |  | 8.7208 |  | 8.2208 |  | 7.7208 |  | 6.208 |  | 5.708
1990-04-23 | 32.1208 | 31.2189 | 26.6113 | 24.5 | 25 | 25.5 | 27.1113 | 27.6113 | 5.5095 |  | 7.6208 |  | 7.1208 |  | 6.6208 |  | 5.0095 |  | 4.5095
1990-04-24 | 29.3583 | 31.4808 | 26.6846 | 24.5 | 25 | 25.5 | 27.1846 | 27.6846 | 2.6737 |  | 4.8583 |  | 4.3583 |  | 3.8583 |  | 2.1737 |  | 1.6737
1990-04-25 | 31.2917 | 31.5697 | 26.7095 | 24.5 | 25 | 25.5 | 27.2095 | 27.7095 | 4.5821 |  | 6.7917 |  | 6.2917 |  | 5.7917 |  | 4.0821 |  | 3.5821
1990-04-26 | 32.9875 | 31.6776 | 26.7397 | 24.5 | 25 | 25.5 | 27.2397 | 27.7397 | 6.2478 |  | 8.4875 |  | 7.9875 |  | 7.4875 |  | 5.7478 |  | 5.2478
1990-04-27 | 34.8042 | 31.8231 | 26.7805 | 24.5 | 25 | 25.5 | 27.2805 | 27.7805 | 8.0237 |  | 10.3042 |  | 9.8042 |  | 9.3042 |  | 7.5237 |  | 7.0237
1990-04-28 | 35.5667 | 31.9635 | 26.8198 | 24.5 | 25 | 25.5 | 27.3198 | 27.8198 | 8.7469 |  | 11.0667 |  | 10.5667 |  | 10.0667 |  | 8.2469 |  | 7.7469
1990-04-29 | 35.1708 | 32.0856 | 26.854 | 24.5 | 25 | 25.5 | 27.354 | 27.854 | 8.3169 |  | 10.6708 |  | 10.1708 |  | 9.6708 |  | 7.8169 |  | 7.3169
1990-04-30 | 34.2833 | 32.2029 | 26.8868 | 24.5 | 25 | 25.5 | 27.3868 | 27.8868 | 7.3965 |  | 9.7833 |  | 9.2833 |  | 8.7833 |  | 6.8965 |  | 6.3965
1990-05-01 | 34.575 | 32.3128 | 26.9176 | 24.5 | 25 | 25.5 | 27.4176 | 27.9176 | 7.6574 |  | 10.075 |  | 9.575 |  | 9.075 |  | 7.1574 |  | 6.6574
1990-05-02 | 36 | 32.5265 | 26.9774 | 24.5 | 25 | 25.5 | 27.4774 | 27.9774 | 9.0226 |  | 11.5 |  | 11 |  | 10.5 |  | 8.5226 |  | 8.0226
1990-05-03 | 37.4167 | 32.7386 | 27.0368 | 24.5 | 25 | 25.5 | 27.5368 | 28.0368 | 10.3799 |  | 12.9167 |  | 12.4167 |  | 11.9167 |  | 9.8799 |  | 9.3799
1990-05-04 | 36.8708 | 33.0772 | 27.1316 | 24.5 | 25 | 25.5 | 27.6316 | 28.1316 | 9.7392 |  | 12.3708 |  | 11.8708 |  | 11.3708 |  | 9.2392 |  | 8.7392
1990-05-05 | 36.1042 | 33.4089 | 27.2245 | 24.5 | 25 | 25.5 | 27.7245 | 28.2245 | 8.8797 |  | 11.6042 |  | 11.1042 |  | 10.6042 |  | 8.3797 |  | 7.8797
1990-05-06 | 35.0417 | 33.6326 | 27.2871 | 24.5 | 25 | 25.5 | 27.7871 | 28.2871 | 7.7545 |  | 10.5417 |  | 10.0417 |  | 9.5417 |  | 7.2545 |  | 6.7545
1990-05-07 | 32.875 | 33.8456 | 27.3468 | 24.5 | 25 | 25.5 | 27.8468 | 28.3468 | 5.5282 |  | 8.375 |  | 7.875 |  | 7.375 |  | 5.0282 |  | 4.5282
1990-05-08 | 31.9708 | 33.9404 | 27.3733 | 24.5 | 25 | 25.5 | 27.8733 | 28.3733 | 4.5975 |  | 7.4708 |  | 6.9708 |  | 6.4708 |  | 4.0975 |  | 3.5975
1990-05-09 | 28.825 | 33.9532 | 27.3769 | 24.5 | 25 | 25.5 | 27.8769 | 28.3769 | 1.4481 |  | 4.325 |  | 3.825 |  | 3.325 |  | 0.94811 |  | 0.44811
1990-05-10 | 29.4667 | 33.8175 | 27.3389 | 24.5 | 25 | 25.5 | 27.8389 | 28.3389 | 2.1278 |  | 4.9667 |  | 4.4667 |  | 3.9667 |  | 1.6278 |  | 1.1278
1990-05-11 | 32.3833 | 33.7128 | 27.3096 | 24.5 | 25 | 25.5 | 27.8096 | 28.3096 | 5.0738 |  | 7.8833 |  | 7.3833 |  | 6.8833 |  | 4.5738 |  | 4.0738
1990-05-12 | 35.5833 | 33.691 | 27.3035 | 24.5 | 25 | 25.5 | 27.8035 | 28.3035 | 8.2799 |  | 11.0833 |  | 10.5833 |  | 10.0833 |  | 7.7799 |  | 7.2799
1990-05-13 | 36.4625 | 33.7638 | 27.3239 | 24.5 | 25 | 25.5 | 27.8239 | 28.3239 | 9.1386 |  | 11.9625 |  | 11.4625 |  | 10.9625 |  | 8.6386 |  | 8.1386
1990-05-14 | 37.4375 | 33.8514 | 27.3484 | 24.5 | 25 | 25.5 | 27.8484 | 28.3484 | 10.0891 |  | 12.9375 |  | 12.4375 |  | 11.9375 |  | 9.5891 |  | 9.0891
1990-05-15 | 37.4625 | 33.9567 | 27.3779 | 24.5 | 25 | 25.5 | 27.8779 | 28.3779 | 10.0846 |  | 12.9625 |  | 12.4625 |  | 11.9625 |  | 9.5846 |  | 9.0846
1990-05-16 | 37.9292 | 34.0369 | 27.4003 | 24.5 | 25 | 25.5 | 27.9003 | 28.4003 | 10.5288 |  | 13.4292 |  | 12.9292 |  | 12.4292 |  | 10.0288 |  | 9.5288
1990-05-17 | 38.7208 | 34.11 | 27.4208 | 24.5 | 25 | 25.5 | 27.9208 | 28.4208 | 11.3 |  | 14.2208 |  | 13.7208 |  | 13.2208 |  | 10.8 |  | 10.3
1990-05-18 | 37.6708 | 34.2132 | 27.4497 | 24.5 | 25 | 25.5 | 27.9497 | 28.4497 | 10.2211 |  | 13.1708 |  | 12.6708 |  | 12.1708 |  | 9.7211 |  | 9.2211
1990-05-19 | 38.3875 | 34.3396 | 27.4851 | 24.5 | 25 | 25.5 | 27.9851 | 28.4851 | 10.9024 |  | 13.8875 |  | 13.3875 |  | 12.8875 |  | 10.4024 |  | 9.9024
1990-05-20 | 37.0333 | 34.536 | 27.5401 | 24.5 | 25 | 25.5 | 28.0401 | 28.5401 | 9.4933 |  | 12.5333 |  | 12.0333 |  | 11.5333 |  | 8.9933 |  | 8.4933
1990-05-21 | 37.9333 | 34.6771 | 27.5796 | 24.5 | 25 | 25.5 | 28.0796 | 28.5796 | 10.3537 |  | 13.4333 |  | 12.9333 |  | 12.4333 |  | 9.8537 |  | 9.3537
1990-05-22 | 37.8958 | 34.8318 | 27.6229 | 24.5 | 25 | 25.5 | 28.1229 | 28.6229 | 10.2729 |  | 13.3958 |  | 12.8958 |  | 12.3958 |  | 9.7729 |  | 9.2729
1990-05-23 | 37.0667 | 34.9876 | 27.6665 | 24.5 | 25 | 25.5 | 28.1665 | 28.6665 | 9.4001 |  | 12.5667 |  | 12.0667 |  | 11.5667 |  | 8.9001 |  | 8.4001
1990-05-24 | 38.2667 | 35.1525 | 27.7127 | 24.5 | 25 | 25.5 | 28.2127 | 28.7127 | 10.554 |  | 13.7667 |  | 13.2667 |  | 12.7667 |  | 10.054 |  | 9.554
1990-05-25 | 37.7542 | 35.4494 | 27.7958 | 24.5 | 25 | 25.5 | 28.2958 | 28.7958 | 9.9583 |  | 13.2542 |  | 12.7542 |  | 12.2542 |  | 9.4583 |  | 8.9583
1990-05-26 | 37.95 | 35.6649 | 27.8562 | 24.5 | 25 | 25.5 | 28.3562 | 28.8562 | 10.0938 |  | 13.45 |  | 12.95 |  | 12.45 |  | 9.5938 |  | 9.0938
1990-05-27 | 38.4208 | 35.8303 | 27.9025 | 24.5 | 25 | 25.5 | 28.4025 | 28.9025 | 10.5184 |  | 13.9208 |  | 13.4208 |  | 12.9208 |  | 10.0184 |  | 9.5184
1990-05-28 | 38.1458 | 35.9508 | 27.9362 | 24.5 | 25 | 25.5 | 28.4362 | 28.9362 | 10.2096 |  | 13.6458 |  | 13.1458 |  | 12.6458 |  | 9.7096 |  | 9.2096
1990-05-29 | 38.1583 | 36.0368 | 27.9603 | 24.5 | 25 | 25.5 | 28.4603 | 28.9603 | 10.198 |  | 13.6583 |  | 13.1583 |  | 12.6583 |  | 9.698 |  | 9.198
1990-05-30 | 38.8375 | 36.1364 | 27.9882 | 24.5 | 25 | 25.5 | 28.4882 | 28.9882 | 10.8493 |  | 14.3375 |  | 13.8375 |  | 13.3375 |  | 10.3493 |  | 9.8493
1990-05-31 | 39.7917 | 36.2882 | 28.0307 | 24.5 | 25 | 25.5 | 28.5307 | 29.0307 | 11.761 |  | 15.2917 |  | 14.7917 |  | 14.2917 |  | 11.261 |  | 10.761
1990-06-01 | 38.5958 | 36.4621 | 28.0794 | 24.5 | 25 | 25.5 | 28.5794 | 29.0794 | 10.5164 |  | 14.0958 |  | 13.5958 |  | 13.0958 |  | 10.0164 |  | 9.5164
1990-06-02 | 37.8083 | 36.5486 | 28.1036 | 24.5 | 25 | 25.5 | 28.6036 | 29.1036 | 9.7047 |  | 13.3083 |  | 12.8083 |  | 12.3083 |  | 9.2047 |  | 8.7047
1990-06-03 | 36.9625 | 36.5617 | 28.1073 | 24.5 | 25 | 25.5 | 28.6073 | 29.1073 | 8.8552 |  | 12.4625 |  | 11.9625 |  | 11.4625 |  | 8.3552 |  | 7.8552
1990-06-04 | 37.7208 | 36.5647 | 28.1081 | 24.5 | 25 | 25.5 | 28.6081 | 29.1081 | 9.6127 |  | 13.2208 |  | 12.7208 |  | 12.2208 |  | 9.1127 |  | 8.6127
1990-06-05 | 38.3208 | 36.6186 | 28.1232 | 24.5 | 25 | 25.5 | 28.6232 | 29.1232 | 10.1976 |  | 13.8208 |  | 13.3208 |  | 12.8208 |  | 9.6976 |  | 9.1976
1990-06-06 | 37.4292 | 36.7279 | 28.1538 | 24.5 | 25 | 25.5 | 28.6538 | 29.1538 | 9.2754 |  | 12.9292 |  | 12.4292 |  | 11.9292 |  | 8.7754 |  | 8.2754
1990-06-07 | 36.3208 | 36.8797 | 28.1963 | 24.5 | 25 | 25.5 | 28.6963 | 29.1963 | 8.1245 |  | 11.8208 |  | 11.3208 |  | 10.8208 |  | 7.6245 |  | 7.1245
1990-06-08 | 35.5667 | 37.0247 | 28.2369 | 24.5 | 25 | 25.5 | 28.7369 | 29.2369 | 7.3297 |  | 11.0667 |  | 10.5667 |  | 10.0667 |  | 6.8297 |  | 6.3297
1990-06-09 | 32.4625 | 37.2494 | 28.2998 | 24.5 | 25 | 25.5 | 28.7998 | 29.2998 | 4.1627 |  | 7.9625 |  | 7.4625 |  | 6.9625 |  | 3.6627 |  | 3.1627
1990-06-10 | 32.2583 | 37.3493 | 28.3278 | 24.5 | 25 | 25.5 | 28.8278 | 29.3278 | 3.9305 |  | 7.7583 |  | 7.2583 |  | 6.7583 |  | 3.4305 |  | 2.9305
1990-06-11 | 32.4667 | 37.3451 | 28.3266 | 24.5 | 25 | 25.5 | 28.8266 | 29.3266 | 4.14 |  | 7.9667 |  | 7.4667 |  | 6.9667 |  | 3.64 |  | 3.14
1990-06-12 | 27.8875 | 37.2413 | 28.2976 | 24.5 | 25 | 25.5 | 28.7976 | 29.2976 | 0 |  | 3.3875 |  | 2.8875 |  | 2.3875 |  | 0 |  | 0
1990-06-13 | 31.225 | 36.9554 | 28.2175 | 24.5 | 25 | 25.5 | 28.7175 | 29.2175 | 3.0075 |  | 6.725 |  | 6.225 |  | 5.725 |  | 2.5075 |  | 2.0075
1990-06-14 | 33.3875 | 36.7483 | 28.1595 | 24.5 | 25 | 25.5 | 28.6595 | 29.1595 | 5.228 |  | 8.8875 |  | 8.3875 |  | 7.8875 |  | 4.728 |  | 4.228
1990-06-15 | 36.3375 | 36.6125 | 28.1215 | 24.5 | 25 | 25.5 | 28.6215 | 29.1215 | 8.216 |  | 11.8375 |  | 11.3375 |  | 10.8375 |  | 7.716 |  | 7.216
1990-06-16 | 35.75 | 36.5594 | 28.1066 | 24.5 | 25 | 25.5 | 28.6066 | 29.1066 | 7.6434 |  | 11.25 |  | 10.75 |  | 10.25 |  | 7.1434 |  | 6.6434
1990-06-17 | 36.3125 | 36.4604 | 28.0789 | 24.5 | 25 | 25.5 | 28.5789 | 29.0789 | 8.2336 |  | 11.8125 |  | 11.3125 |  | 10.8125 |  | 7.7336 |  | 7.2336
1990-06-18 | 34.4167 | 36.4151 | 28.0662 | 24.5 | 25 | 25.5 | 28.5662 | 29.0662 | 6.3504 |  | 9.9167 |  | 9.4167 |  | 8.9167 |  | 5.8504 |  | 5.3504
1990-06-19 | 33.8417 | 36.2828 | 28.0292 | 24.5 | 25 | 25.5 | 28.5292 | 29.0292 | 5.8125 |  | 9.3417 |  | 8.8417 |  | 8.3417 |  | 5.3125 |  | 4.8125
1990-06-20 | 32.7333 | 36.1764 | 27.9994 | 24.5 | 25 | 25.5 | 28.4994 | 28.9994 | 4.7339 |  | 8.2333 |  | 7.7333 |  | 7.2333 |  | 4.2339 |  | 3.7339
1990-06-21 | 33.1208 | 36.0031 | 27.9509 | 24.5 | 25 | 25.5 | 28.4509 | 28.9509 | 5.17 |  | 8.6208 |  | 8.1208 |  | 7.6208 |  | 4.67 |  | 4.17
1990-06-22 | 33.6833 | 35.8439 | 27.9063 | 24.5 | 25 | 25.5 | 28.4063 | 28.9063 | 5.777 |  | 9.1833 |  | 8.6833 |  | 8.1833 |  | 5.277 |  | 4.777
1990-06-23 | 34.7208 | 35.7311 | 27.8747 | 24.5 | 25 | 25.5 | 28.3747 | 28.8747 | 6.8461 |  | 10.2208 |  | 9.7208 |  | 9.2208 |  | 6.3461 |  | 5.8461
1990-06-24 | 34.7667 | 35.6129 | 27.8416 | 24.5 | 25 | 25.5 | 28.3416 | 28.8416 | 6.9251 |  | 10.2667 |  | 9.7667 |  | 9.2667 |  | 6.4251 |  | 5.9251
1990-06-25 | 35.4792 | 35.5133 | 27.8137 | 24.5 | 25 | 25.5 | 28.3137 | 28.8137 | 7.6654 |  | 10.9792 |  | 10.4792 |  | 9.9792 |  | 7.1654 |  | 6.6654
1990-06-26 | 34.3583 | 35.431 | 27.7907 | 24.5 | 25 | 25.5 | 28.2907 | 28.7907 | 6.5677 |  | 9.8583 |  | 9.3583 |  | 8.8583 |  | 6.0677 |  | 5.5677
1990-06-27 | 33.225 | 35.2956 | 27.7528 | 24.5 | 25 | 25.5 | 28.2528 | 28.7528 | 5.4722 |  | 8.725 |  | 8.225 |  | 7.725 |  | 4.9722 |  | 4.4722
1990-06-28 | 32.6208 | 35.1315 | 27.7068 | 24.5 | 25 | 25.5 | 28.2068 | 28.7068 | 4.914 |  | 8.1208 |  | 7.6208 |  | 7.1208 |  | 4.414 |  | 3.914
1990-06-29 | 30.1208 | 34.9469 | 27.6551 | 24.5 | 25 | 25.5 | 28.1551 | 28.6551 | 2.4657 |  | 5.6208 |  | 5.1208 |  | 4.6208 |  | 1.9657 |  | 1.4657
1990-06-30 | 29.5417 | 34.6564 | 27.5738 | 24.5 | 25 | 25.5 | 28.0738 | 28.5738 | 1.9679 |  | 5.0417 |  | 4.5417 |  | 4.0417 |  | 1.4679 |  | 0.96788
1990-07-01 | 30.0042 | 34.3147 | 27.4781 | 24.5 | 25 | 25.5 | 27.9781 | 28.4781 | 2.526 |  | 5.5042 |  | 5.0042 |  | 4.5042 |  | 2.026 |  | 1.526
1990-07-02 | 32.525 | 34.0283 | 27.3979 | 24.5 | 25 | 25.5 | 27.8979 | 28.3979 | 5.1271 |  | 8.025 |  | 7.525 |  | 7.025 |  | 4.6271 |  | 4.1271
1990-07-03 | 32.9542 | 33.8522 | 27.3486 | 24.5 | 25 | 25.5 | 27.8486 | 28.3486 | 5.6055 |  | 8.4542 |  | 7.9542 |  | 7.4542 |  | 5.1055 |  | 4.6055
1990-07-04 | 33.025 | 33.7186 | 27.3112 | 24.5 | 25 | 25.5 | 27.8112 | 28.3112 | 5.7138 |  | 8.525 |  | 8.025 |  | 7.525 |  | 5.2138 |  | 4.7138
1990-07-05 | 32.4792 | 33.5621 | 27.2674 | 24.5 | 25 | 25.5 | 27.7674 | 28.2674 | 5.2118 |  | 7.9792 |  | 7.4792 |  | 6.9792 |  | 4.7118 |  | 4.2118
1990-07-06 | 29.7667 | 33.3674 | 27.2129 | 24.5 | 25 | 25.5 | 27.7129 | 28.2129 | 2.5538 |  | 5.2667 |  | 4.7667 |  | 4.2667 |  | 2.0538 |  | 1.5538
1990-07-07 | 31.1708 | 33.1119 | 27.1413 | 24.5 | 25 | 25.5 | 27.6413 | 28.1413 | 4.0295 |  | 6.6708 |  | 6.1708 |  | 5.6708 |  | 3.5295 |  | 3.0295
1990-07-08 | 27.275 | 32.9403 | 27.0933 | 24.5 | 25 | 25.5 | 27.5933 | 28.0933 | 0.18172 |  | 2.775 |  | 2.275 |  | 1.775 |  | 0 |  | 0
1990-07-09 | 29.025 | 32.6639 | 27.0159 | 24.5 | 25 | 25.5 | 27.5159 | 28.0159 | 2.0091 |  | 4.525 |  | 4.025 |  | 3.525 |  | 1.5091 |  | 1.0091
1990-07-10 | 27.9792 | 32.5493 | 26.9838 | 24.5 | 25 | 25.5 | 27.4838 | 27.9838 | 0.99536 |  | 3.4792 |  | 2.9792 |  | 2.4792 |  | 0.49536 |  | 0
1990-07-11 | 28.6792 | 32.4067 | 26.9439 | 24.5 | 25 | 25.5 | 27.4439 | 27.9439 | 1.7353 |  | 4.1792 |  | 3.6792 |  | 3.1792 |  | 1.2353 |  | 0.7353
1990-07-12 | 29.3375 | 32.2804 | 26.9085 | 24.5 | 25 | 25.5 | 27.4085 | 27.9085 | 2.429 |  | 4.8375 |  | 4.3375 |  | 3.8375 |  | 1.929 |  | 1.429
1990-07-13 | 31.0083 | 32.3287 | 26.9221 | 24.5 | 25 | 25.5 | 27.4221 | 27.9221 | 4.0863 |  | 6.5083 |  | 6.0083 |  | 5.5083 |  | 3.5863 |  | 3.0863
1990-07-14 | 28.05 | 32.3215 | 26.92 | 24.5 | 25 | 25.5 | 27.42 | 27.92 | 1.13 |  | 3.55 |  | 3.05 |  | 2.55 |  | 0.62997 |  | 0.12997
1990-07-15 | 28.8292 | 32.1436 | 26.8702 | 24.5 | 25 | 25.5 | 27.3702 | 27.8702 | 1.959 |  | 4.3292 |  | 3.8292 |  | 3.3292 |  | 1.459 |  | 0.95896
1990-07-16 | 28.85 | 31.8933 | 26.8001 | 24.5 | 25 | 25.5 | 27.3001 | 27.8001 | 2.0499 |  | 4.35 |  | 3.85 |  | 3.35 |  | 1.5499 |  | 1.0499
1990-07-17 | 28.2167 | 31.6633 | 26.7357 | 24.5 | 25 | 25.5 | 27.2357 | 27.7357 | 1.4809 |  | 3.7167 |  | 3.2167 |  | 2.7167 |  | 0.98093 |  | 0.48093
1990-07-18 | 27.5208 | 31.3935 | 26.6602 | 24.5 | 25 | 25.5 | 27.1602 | 27.6602 | 0.86066 |  | 3.0208 |  | 2.5208 |  | 2.0208 |  | 0.36066 |  | 0
1990-07-19 | 29.0375 | 31.1636 | 26.5958 | 24.5 | 25 | 25.5 | 27.0958 | 27.5958 | 2.4417 |  | 4.5375 |  | 4.0375 |  | 3.5375 |  | 1.9417 |  | 1.4417
1990-07-20 | 25.9583 | 31.0035 | 26.551 | 24.5 | 25 | 25.5 | 27.051 | 27.551 | 0 |  | 1.4583 |  | 0.95833 |  | 0.45833 |  | 0 |  | 0
1990-07-21 | 26.0583 | 30.7776 | 26.4877 | 24.5 | 25 | 25.5 | 26.9877 | 27.4877 | 0 |  | 1.5583 |  | 1.0583 |  | 0.55833 |  | 0 |  | 0
1990-07-22 | 28.1417 | 30.5422 | 26.4218 | 24.5 | 25 | 25.5 | 26.9218 | 27.4218 | 1.7198 |  | 3.6417 |  | 3.1417 |  | 2.6417 |  | 1.2198 |  | 0.71984
1990-07-23 | 28.1708 | 30.3575 | 26.3701 | 24.5 | 25 | 25.5 | 26.8701 | 27.3701 | 1.8007 |  | 3.6708 |  | 3.1708 |  | 2.6708 |  | 1.3007 |  | 0.80073
1990-07-24 | 29.5375 | 30.1392 | 26.309 | 24.5 | 25 | 25.5 | 26.809 | 27.309 | 3.2285 |  | 5.0375 |  | 4.5375 |  | 4.0375 |  | 2.7285 |  | 2.2285
1990-07-25 | 29.9208 | 29.9649 | 26.2602 | 24.5 | 25 | 25.5 | 26.7602 | 27.2602 | 3.6607 |  | 5.4208 |  | 4.9208 |  | 4.4208 |  | 3.1607 |  | 2.6607
1990-07-26 | 29.8458 | 29.7796 | 26.2083 | 24.5 | 25 | 25.5 | 26.7083 | 27.2083 | 3.6375 |  | 5.3458 |  | 4.8458 |  | 4.3458 |  | 3.1375 |  | 2.6375
1990-07-27 | 29.4625 | 29.6292 | 26.1662 | 24.5 | 25 | 25.5 | 26.6662 | 27.1662 | 3.2963 |  | 4.9625 |  | 4.4625 |  | 3.9625 |  | 2.7963 |  | 2.2963
1990-07-28 | 28.925 | 29.5037 | 26.1311 | 24.5 | 25 | 25.5 | 26.6311 | 27.1311 | 2.7939 |  | 4.425 |  | 3.925 |  | 3.425 |  | 2.2939 |  | 1.7939
1990-07-29 | 29.1292 | 29.3806 | 26.0966 | 24.5 | 25 | 25.5 | 26.5966 | 27.0966 | 3.0326 |  | 4.6292 |  | 4.1292 |  | 3.6292 |  | 2.5326 |  | 2.0326
1990-07-30 | 29.5542 | 29.3475 | 26.0873 | 24.5 | 25 | 25.5 | 26.5873 | 27.0873 | 3.4669 |  | 5.0542 |  | 4.5542 |  | 4.0542 |  | 2.9669 |  | 2.4669
1990-07-31 | 28.8458 | 29.3479 | 26.0874 | 24.5 | 25 | 25.5 | 26.5874 | 27.0874 | 2.7584 |  | 4.3458 |  | 3.8458 |  | 3.3458 |  | 2.2584 |  | 1.7584
1990-08-01 | 28.3792 | 29.3093 | 26.0766 | 24.5 | 25 | 25.5 | 26.5766 | 27.0766 | 2.3026 |  | 3.8792 |  | 3.3792 |  | 2.8792 |  | 1.8026 |  | 1.3026
1990-08-02 | 27.975 | 29.1711 | 26.0379 | 24.5 | 25 | 25.5 | 26.5379 | 27.0379 | 1.9371 |  | 3.475 |  | 2.975 |  | 2.475 |  | 1.4371 |  | 0.93709
1990-08-03 | 28.1542 | 29.0051 | 25.9914 | 24.5 | 25 | 25.5 | 26.4914 | 26.9914 | 2.1627 |  | 3.6542 |  | 3.1542 |  | 2.6542 |  | 1.6627 |  | 1.1627
1990-08-04 | 29.3708 | 28.8428 | 25.946 | 24.5 | 25 | 25.5 | 26.446 | 26.946 | 3.4249 |  | 4.8708 |  | 4.3708 |  | 3.8708 |  | 2.9249 |  | 2.4249
1990-08-05 | 29.225 | 28.7392 | 25.917 | 24.5 | 25 | 25.5 | 26.417 | 26.917 | 3.308 |  | 4.725 |  | 4.225 |  | 3.725 |  | 2.808 |  | 2.308
1990-08-06 | 29.5375 | 28.7211 | 25.9119 | 24.5 | 25 | 25.5 | 26.4119 | 26.9119 | 3.6256 |  | 5.0375 |  | 4.5375 |  | 4.0375 |  | 3.1256 |  | 2.6256
1990-08-07 | 30.0375 | 28.6667 | 25.8967 | 24.5 | 25 | 25.5 | 26.3967 | 26.8967 | 4.1408 |  | 5.5375 |  | 5.0375 |  | 4.5375 |  | 3.6408 |  | 3.1408
1990-08-08 | 28.5167 | 28.7588 | 25.9225 | 24.5 | 25 | 25.5 | 26.4225 | 26.9225 | 2.5942 |  | 4.0167 |  | 3.5167 |  | 3.0167 |  | 2.0942 |  | 1.5942
1990-08-09 | 27.6625 | 28.7418 | 25.9177 | 24.5 | 25 | 25.5 | 26.4177 | 26.9177 | 1.7448 |  | 3.1625 |  | 2.6625 |  | 2.1625 |  | 1.2448 |  | 0.74479
1990-08-10 | 26.95 | 28.7312 | 25.9148 | 24.5 | 25 | 25.5 | 26.4148 | 26.9148 | 1.0352 |  | 2.45 |  | 1.95 |  | 1.45 |  | 0.53525 |  | 0.03525
1990-08-11 | 25.85 | 28.6736 | 25.8986 | 24.5 | 25 | 25.5 | 26.3986 | 26.8986 | 0 |  | 1.35 |  | 0.85 |  | 0.35 |  | 0 |  | 0
1990-08-12 | 27.8917 | 28.5574 | 25.8661 | 24.5 | 25 | 25.5 | 26.3661 | 26.8661 | 2.0256 |  | 3.3917 |  | 2.8917 |  | 2.3917 |  | 1.5256 |  | 1.0256
1990-08-13 | 28.1375 | 28.4535 | 25.837 | 24.5 | 25 | 25.5 | 26.337 | 26.837 | 2.3005 |  | 3.6375 |  | 3.1375 |  | 2.6375 |  | 1.8005 |  | 1.3005
1990-08-14 | 28.7875 | 28.4564 | 25.8378 | 24.5 | 25 | 25.5 | 26.3378 | 26.8378 | 2.9497 |  | 4.2875 |  | 3.7875 |  | 3.2875 |  | 2.4497 |  | 1.9497
1990-08-15 | 28.9292 | 28.455 | 25.8374 | 24.5 | 25 | 25.5 | 26.3374 | 26.8374 | 3.0918 |  | 4.4292 |  | 3.9292 |  | 3.4292 |  | 2.5918 |  | 2.0918
1990-08-16 | 26.8792 | 28.4576 | 25.8381 | 24.5 | 25 | 25.5 | 26.3381 | 26.8381 | 1.041 |  | 2.3792 |  | 1.8792 |  | 1.3792 |  | 0.54103 |  | 0.041028
1990-08-17 | 26.75 | 28.4131 | 25.8257 | 24.5 | 25 | 25.5 | 26.3257 | 26.8257 | 0.92434 |  | 2.25 |  | 1.75 |  | 1.25 |  | 0.42434 |  | 0
1990-08-18 | 28.325 | 28.3874 | 25.8185 | 24.5 | 25 | 25.5 | 26.3185 | 26.8185 | 2.5065 |  | 3.825 |  | 3.325 |  | 2.825 |  | 2.0065 |  | 1.5065
1990-08-19 | 27.9042 | 28.3636 | 25.8118 | 24.5 | 25 | 25.5 | 26.3118 | 26.8118 | 2.0924 |  | 3.4042 |  | 2.9042 |  | 2.4042 |  | 1.5924 |  | 1.0924
1990-08-20 | 28.425 | 28.4285 | 25.83 | 24.5 | 25 | 25.5 | 26.33 | 26.83 | 2.595 |  | 3.925 |  | 3.425 |  | 2.925 |  | 2.095 |  | 1.595
1990-08-21 | 26.8833 | 28.5074 | 25.8521 | 24.5 | 25 | 25.5 | 26.3521 | 26.8521 | 1.0313 |  | 2.3833 |  | 1.8833 |  | 1.3833 |  | 0.53127 |  | 0.031272
1990-08-22 | 26.4792 | 28.4654 | 25.8403 | 24.5 | 25 | 25.5 | 26.3403 | 26.8403 | 0.63885 |  | 1.9792 |  | 1.4792 |  | 0.97917 |  | 0.13885 |  | 0
1990-08-23 | 24.9458 | 28.409 | 25.8245 | 24.5 | 25 | 25.5 | 26.3245 | 26.8245 | 0 |  | 0.44583 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-24 | 26.6792 | 28.256 | 25.7817 | 24.5 | 25 | 25.5 | 26.2817 | 26.7817 | 0.89749 |  | 2.1792 |  | 1.6792 |  | 1.1792 |  | 0.39749 |  | 0
1990-08-25 | 27.6083 | 28.1479 | 25.7514 | 24.5 | 25 | 25.5 | 26.2514 | 26.7514 | 1.8569 |  | 3.1083 |  | 2.6083 |  | 2.1083 |  | 1.3569 |  | 0.85692
1990-08-26 | 27.6333 | 28.0733 | 25.7305 | 24.5 | 25 | 25.5 | 26.2305 | 26.7305 | 1.9028 |  | 3.1333 |  | 2.6333 |  | 2.1333 |  | 1.4028 |  | 0.9028
1990-08-27 | 28.075 | 28.0124 | 25.7135 | 24.5 | 25 | 25.5 | 26.2135 | 26.7135 | 2.3615 |  | 3.575 |  | 3.075 |  | 2.575 |  | 1.8615 |  | 1.3615
1990-08-28 | 27.5417 | 27.984 | 25.7055 | 24.5 | 25 | 25.5 | 26.2055 | 26.7055 | 1.8361 |  | 3.0417 |  | 2.5417 |  | 2.0417 |  | 1.3361 |  | 0.83614
1990-08-29 | 28.7458 | 27.9311 | 25.6907 | 24.5 | 25 | 25.5 | 26.1907 | 26.6907 | 3.0551 |  | 4.2458 |  | 3.7458 |  | 3.2458 |  | 2.5551 |  | 2.0551
1990-08-30 | 29.6167 | 27.9042 | 25.6832 | 24.5 | 25 | 25.5 | 26.1832 | 26.6832 | 3.9335 |  | 5.1167 |  | 4.6167 |  | 4.1167 |  | 3.4335 |  | 2.9335
1990-08-31 | 29.6875 | 27.9299 | 25.6904 | 24.5 | 25 | 25.5 | 26.1904 | 26.6904 | 3.9971 |  | 5.1875 |  | 4.6875 |  | 4.1875 |  | 3.4971 |  | 2.9971
1990-09-01 | 27.4375 | 27.9735 | 25.7026 | 24.5 | 25 | 25.5 | 26.2026 | 26.7026 | 1.7349 |  | 2.9375 |  | 2.4375 |  | 1.9375 |  | 1.2349 |  | 0.73493
1990-09-02 | 27.9833 | 27.9556 | 25.6976 | 24.5 | 25 | 25.5 | 26.1976 | 26.6976 | 2.2858 |  | 3.4833 |  | 2.9833 |  | 2.4833 |  | 1.7858 |  | 1.2858
1990-09-03 | 27.4 | 27.9499 | 25.696 | 24.5 | 25 | 25.5 | 26.196 | 26.696 | 1.704 |  | 2.9 |  | 2.4 |  | 1.9 |  | 1.204 |  | 0.70404
1990-09-04 | 26.4625 | 27.8842 | 25.6776 | 24.5 | 25 | 25.5 | 26.1776 | 26.6776 | 0.78493 |  | 1.9625 |  | 1.4625 |  | 0.9625 |  | 0.28493 |  | 0
1990-09-05 | 27.4083 | 27.7921 | 25.6518 | 24.5 | 25 | 25.5 | 26.1518 | 26.6518 | 1.7565 |  | 2.9083 |  | 2.4083 |  | 1.9083 |  | 1.2565 |  | 0.75655
1990-09-06 | 26.9083 | 27.7211 | 25.6319 | 24.5 | 25 | 25.5 | 26.1319 | 26.6319 | 1.2764 |  | 2.4083 |  | 1.9083 |  | 1.4083 |  | 0.77642 |  | 0.27642
1990-09-07 | 26.9667 | 27.6168 | 25.6027 | 24.5 | 25 | 25.5 | 26.1027 | 26.6027 | 1.364 |  | 2.4667 |  | 1.9667 |  | 1.4667 |  | 0.86396 |  | 0.36396
1990-09-08 | 27.2167 | 27.5651 | 25.5882 | 24.5 | 25 | 25.5 | 26.0882 | 26.5882 | 1.6284 |  | 2.7167 |  | 2.2167 |  | 1.7167 |  | 1.1284 |  | 0.62843
1990-09-09 | 27.6 | 27.5503 | 25.5841 | 24.5 | 25 | 25.5 | 26.0841 | 26.5841 | 2.0159 |  | 3.1 |  | 2.6 |  | 2.1 |  | 1.5159 |  | 1.0159
1990-09-10 | 28.0292 | 27.5719 | 25.5901 | 24.5 | 25 | 25.5 | 26.0901 | 26.5901 | 2.439 |  | 3.5292 |  | 3.0292 |  | 2.5292 |  | 1.939 |  | 1.439
1990-09-11 | 28.4792 | 27.6446 | 25.6105 | 24.5 | 25 | 25.5 | 26.1105 | 26.6105 | 2.8687 |  | 3.9792 |  | 3.4792 |  | 2.9792 |  | 2.3687 |  | 1.8687
1990-09-12 | 29.3375 | 27.6642 | 25.616 | 24.5 | 25 | 25.5 | 26.116 | 26.616 | 3.7215 |  | 4.8375 |  | 4.3375 |  | 3.8375 |  | 3.2215 |  | 2.7215
1990-09-13 | 28.9333 | 27.7042 | 25.6272 | 24.5 | 25 | 25.5 | 26.1272 | 26.6272 | 3.3062 |  | 4.4333 |  | 3.9333 |  | 3.4333 |  | 2.8062 |  | 2.3062
1990-09-14 | 27.875 | 27.709 | 25.6285 | 24.5 | 25 | 25.5 | 26.1285 | 26.6285 | 2.2465 |  | 3.375 |  | 2.875 |  | 2.375 |  | 1.7465 |  | 1.2465
1990-09-15 | 26.7458 | 27.6739 | 25.6187 | 24.5 | 25 | 25.5 | 26.1187 | 26.6187 | 1.1271 |  | 2.2458 |  | 1.7458 |  | 1.2458 |  | 0.62714 |  | 0.12714
1990-09-16 | 28.0625 | 27.6694 | 25.6174 | 24.5 | 25 | 25.5 | 26.1174 | 26.6174 | 2.4451 |  | 3.5625 |  | 3.0625 |  | 2.5625 |  | 1.9451 |  | 1.4451
1990-09-17 | 29.5167 | 27.7132 | 25.6297 | 24.5 | 25 | 25.5 | 26.1297 | 26.6297 | 3.887 |  | 5.0167 |  | 4.5167 |  | 4.0167 |  | 3.387 |  | 2.887
1990-09-18 | 28.4042 | 27.7529 | 25.6408 | 24.5 | 25 | 25.5 | 26.1408 | 26.6408 | 2.7634 |  | 3.9042 |  | 3.4042 |  | 2.9042 |  | 2.2634 |  | 1.7634
1990-09-19 | 30.5083 | 27.7696 | 25.6455 | 24.5 | 25 | 25.5 | 26.1455 | 26.6455 | 4.8628 |  | 6.0083 |  | 5.5083 |  | 5.0083 |  | 4.3628 |  | 3.8628
1990-09-20 | 29.0167 | 27.839 | 25.6649 | 24.5 | 25 | 25.5 | 26.1649 | 26.6649 | 3.3517 |  | 4.5167 |  | 4.0167 |  | 3.5167 |  | 2.8517 |  | 2.3517
1990-09-21 | 30.0292 | 27.9101 | 25.6848 | 24.5 | 25 | 25.5 | 26.1848 | 26.6848 | 4.3443 |  | 5.5292 |  | 5.0292 |  | 4.5292 |  | 3.8443 |  | 3.3443
1990-09-22 | 30.7167 | 28.0285 | 25.718 | 24.5 | 25 | 25.5 | 26.218 | 26.718 | 4.9987 |  | 6.2167 |  | 5.7167 |  | 5.2167 |  | 4.4987 |  | 3.9987
1990-09-23 | 30.9125 | 28.2208 | 25.7718 | 24.5 | 25 | 25.5 | 26.2718 | 26.7718 | 5.1407 |  | 6.4125 |  | 5.9125 |  | 5.4125 |  | 4.6407 |  | 4.1407
1990-09-24 | 29.7625 | 28.3619 | 25.8113 | 24.5 | 25 | 25.5 | 26.3113 | 26.8113 | 3.9512 |  | 5.2625 |  | 4.7625 |  | 4.2625 |  | 3.4512 |  | 2.9512
1990-09-25 | 30.8958 | 28.4337 | 25.8315 | 24.5 | 25 | 25.5 | 26.3315 | 26.8315 | 5.0644 |  | 6.3958 |  | 5.8958 |  | 5.3958 |  | 4.5644 |  | 4.0644
1990-09-26 | 30.8917 | 28.5425 | 25.8619 | 24.5 | 25 | 25.5 | 26.3619 | 26.8619 | 5.0298 |  | 6.3917 |  | 5.8917 |  | 5.3917 |  | 4.5298 |  | 4.0298
1990-09-27 | 31.5625 | 28.6364 | 25.8882 | 24.5 | 25 | 25.5 | 26.3882 | 26.8882 | 5.6743 |  | 7.0625 |  | 6.5625 |  | 6.0625 |  | 5.1743 |  | 4.6743
1990-09-28 | 30.1833 | 28.7704 | 25.9257 | 24.5 | 25 | 25.5 | 26.4257 | 26.9257 | 4.2576 |  | 5.6833 |  | 5.1833 |  | 4.6833 |  | 3.7576 |  | 3.2576
1990-09-29 | 30.1125 | 28.8183 | 25.9391 | 24.5 | 25 | 25.5 | 26.4391 | 26.9391 | 4.1734 |  | 5.6125 |  | 5.1125 |  | 4.6125 |  | 3.6734 |  | 3.1734
1990-09-30 | 29.9542 | 28.8349 | 25.9438 | 24.5 | 25 | 25.5 | 26.4438 | 26.9438 | 4.0104 |  | 5.4542 |  | 4.9542 |  | 4.4542 |  | 3.5104 |  | 3.0104
1990-10-01 | 29.7542 | 28.8437 | 25.9462 | 24.5 | 25 | 25.5 | 26.4462 | 26.9462 | 3.8079 |  | 5.2542 |  | 4.7542 |  | 4.2542 |  | 3.3079 |  | 2.8079
1990-10-02 | 30.0125 | 28.921 | 25.9679 | 24.5 | 25 | 25.5 | 26.4679 | 26.9679 | 4.0446 |  | 5.5125 |  | 5.0125 |  | 4.5125 |  | 3.5446 |  | 3.0446
1990-10-03 | 30.1833 | 28.9886 | 25.9868 | 24.5 | 25 | 25.5 | 26.4868 | 26.9868 | 4.1965 |  | 5.6833 |  | 5.1833 |  | 4.6833 |  | 3.6965 |  | 3.1965
1990-10-04 | 29.4667 | 29.0814 | 26.0128 | 24.5 | 25 | 25.5 | 26.5128 | 27.0128 | 3.4539 |  | 4.9667 |  | 4.4667 |  | 3.9667 |  | 2.9539 |  | 2.4539
1990-10-05 | 29.175 | 29.1815 | 26.0408 | 24.5 | 25 | 25.5 | 26.5408 | 27.0408 | 3.1342 |  | 4.675 |  | 4.175 |  | 3.675 |  | 2.6342 |  | 2.1342
1990-10-06 | 27.95 | 29.2404 | 26.0573 | 24.5 | 25 | 25.5 | 26.5573 | 27.0573 | 1.8927 |  | 3.45 |  | 2.95 |  | 2.45 |  | 1.3927 |  | 0.89268
1990-10-07 | 28.0083 | 29.2751 | 26.067 | 24.5 | 25 | 25.5 | 26.567 | 27.067 | 1.9413 |  | 3.5083 |  | 3.0083 |  | 2.5083 |  | 1.4413 |  | 0.94129
1990-10-08 | 28.025 | 29.3099 | 26.0768 | 24.5 | 25 | 25.5 | 26.5768 | 27.0768 | 1.9482 |  | 3.525 |  | 3.025 |  | 2.525 |  | 1.4482 |  | 0.94824
1990-10-09 | 28.9958 | 29.3368 | 26.0843 | 24.5 | 25 | 25.5 | 26.5843 | 27.0843 | 2.9115 |  | 4.4958 |  | 3.9958 |  | 3.4958 |  | 2.4115 |  | 1.9115
1990-10-10 | 28.7125 | 29.3833 | 26.0973 | 24.5 | 25 | 25.5 | 26.5973 | 27.0973 | 2.6152 |  | 4.2125 |  | 3.7125 |  | 3.2125 |  | 2.1152 |  | 1.6152
1990-10-11 | 27.2583 | 29.4061 | 26.1037 | 24.5 | 25 | 25.5 | 26.6037 | 27.1037 | 1.1546 |  | 2.7583 |  | 2.2583 |  | 1.7583 |  | 0.65462 |  | 0.15462
1990-10-12 | 27.8583 | 29.3654 | 26.0923 | 24.5 | 25 | 25.5 | 26.5923 | 27.0923 | 1.766 |  | 3.3583 |  | 2.8583 |  | 2.3583 |  | 1.266 |  | 0.76602
1990-10-13 | 27.2208 | 29.3161 | 26.0785 | 24.5 | 25 | 25.5 | 26.5785 | 27.0785 | 1.1423 |  | 2.7208 |  | 2.2208 |  | 1.7208 |  | 0.64232 |  | 0.14232
1990-10-14 | 28.1208 | 29.259 | 26.0625 | 24.5 | 25 | 25.5 | 26.5625 | 27.0625 | 2.0583 |  | 3.6208 |  | 3.1208 |  | 2.6208 |  | 1.5583 |  | 1.0583
1990-10-15 | 28.0125 | 29.2672 | 26.0648 | 24.5 | 25 | 25.5 | 26.5648 | 27.0648 | 1.9477 |  | 3.5125 |  | 3.0125 |  | 2.5125 |  | 1.4477 |  | 0.94768
1990-10-16 | 27.3708 | 29.3094 | 26.0766 | 24.5 | 25 | 25.5 | 26.5766 | 27.0766 | 1.2942 |  | 2.8708 |  | 2.3708 |  | 1.8708 |  | 0.79419 |  | 0.29419
1990-10-17 | 27.0208 | 29.2864 | 26.0702 | 24.5 | 25 | 25.5 | 26.5702 | 27.0702 | 0.95064 |  | 2.5208 |  | 2.0208 |  | 1.5208 |  | 0.45064 |  | 0
1990-10-18 | 26.7167 | 29.2032 | 26.0469 | 24.5 | 25 | 25.5 | 26.5469 | 27.0469 | 0.66977 |  | 2.2167 |  | 1.7167 |  | 1.2167 |  | 0.16977 |  | 0
1990-10-19 | 27.0917 | 29.1469 | 26.0311 | 24.5 | 25 | 25.5 | 26.5311 | 27.0311 | 1.0605 |  | 2.5917 |  | 2.0917 |  | 1.5917 |  | 0.56052 |  | 0.060522
1990-10-20 | 26.9708 | 29.0331 | 25.9993 | 24.5 | 25 | 25.5 | 26.4993 | 26.9993 | 0.97158 |  | 2.4708 |  | 1.9708 |  | 1.4708 |  | 0.47158 |  | 0
1990-10-21 | 26.8042 | 28.9649 | 25.9802 | 24.5 | 25 | 25.5 | 26.4802 | 26.9802 | 0.82401 |  | 2.3042 |  | 1.8042 |  | 1.3042 |  | 0.32401 |  | 0
1990-10-22 | 27.3083 | 28.8574 | 25.9501 | 24.5 | 25 | 25.5 | 26.4501 | 26.9501 | 1.3583 |  | 2.8083 |  | 2.3083 |  | 1.8083 |  | 0.85827 |  | 0.35827
1990-10-23 | 27.9625 | 28.7437 | 25.9183 | 24.5 | 25 | 25.5 | 26.4183 | 26.9183 | 2.0442 |  | 3.4625 |  | 2.9625 |  | 2.4625 |  | 1.5442 |  | 1.0442
1990-10-24 | 28.0625 | 28.6454 | 25.8907 | 24.5 | 25 | 25.5 | 26.3907 | 26.8907 | 2.1718 |  | 3.5625 |  | 3.0625 |  | 2.5625 |  | 1.6718 |  | 1.1718
1990-10-25 | 28.2542 | 28.5887 | 25.8748 | 24.5 | 25 | 25.5 | 26.3748 | 26.8748 | 2.3793 |  | 3.7542 |  | 3.2542 |  | 2.7542 |  | 1.8793 |  | 1.3793
1990-10-26 | 28.4792 | 28.5007 | 25.8502 | 24.5 | 25 | 25.5 | 26.3502 | 26.8502 | 2.629 |  | 3.9792 |  | 3.4792 |  | 2.9792 |  | 2.129 |  | 1.629
1990-10-27 | 27.5708 | 28.4203 | 25.8277 | 24.5 | 25 | 25.5 | 26.3277 | 26.8277 | 1.7432 |  | 3.0708 |  | 2.5708 |  | 2.0708 |  | 1.2432 |  | 0.74316
1990-10-28 | 26.4417 | 28.2872 | 25.7904 | 24.5 | 25 | 25.5 | 26.2904 | 26.7904 | 0.65124 |  | 1.9417 |  | 1.4417 |  | 0.94167 |  | 0.15124 |  | 0
1990-10-29 | 25.8792 | 28.1625 | 25.7555 | 24.5 | 25 | 25.5 | 26.2555 | 26.7555 | 0.12367 |  | 1.3792 |  | 0.87917 |  | 0.37917 |  | 0 |  | 0
1990-10-30 | 26.1167 | 28.0214 | 25.716 | 24.5 | 25 | 25.5 | 26.216 | 26.716 | 0.40068 |  | 1.6167 |  | 1.1167 |  | 0.61667 |  | 0 |  | 0
1990-10-31 | 24.9958 | 27.8935 | 25.6802 | 24.5 | 25 | 25.5 | 26.1802 | 26.6802 | 0 |  | 0.49583 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-01 | 24.8542 | 27.7349 | 25.6358 | 24.5 | 25 | 25.5 | 26.1358 | 26.6358 | 0 |  | 0.35417 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-02 | 25.0875 | 27.5629 | 25.5876 | 24.5 | 25 | 25.5 | 26.0876 | 26.5876 | 0 |  | 0.5875 |  | 0.0875 |  | 0 |  | 0 |  | 0
1990-11-03 | 25.3708 | 27.3931 | 25.5401 | 24.5 | 25 | 25.5 | 26.0401 | 26.5401 | 0 |  | 0.87083 |  | 0.37083 |  | 0 |  | 0 |  | 0
1990-11-04 | 24.45 | 27.2565 | 25.5018 | 24.5 | 25 | 25.5 | 26.0018 | 26.5018 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-05 | 25.0042 | 27.099 | 25.4577 | 24.5 | 25 | 25.5 | 25.9577 | 26.4577 | 0 |  | 0.50417 |  | 0.0041667 |  | 0 |  | 0 |  | 0
1990-11-06 | 25.1833 | 27.0008 | 25.4302 | 24.5 | 25 | 25.5 | 25.9302 | 26.4302 | 0 |  | 0.68333 |  | 0.18333 |  | 0 |  | 0 |  | 0
1990-11-07 | 25.0708 | 26.9067 | 25.4039 | 24.5 | 25 | 25.5 | 25.9039 | 26.4039 | 0 |  | 0.57083 |  | 0.070833 |  | 0 |  | 0 |  | 0
1990-11-08 | 19.8292 | 26.8082 | 25.3763 | 24.5 | 25 | 25.5 | 25.8763 | 26.3763 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-09 | 19.0833 | 26.5026 | 25.2907 | 24.5 | 25 | 25.5 | 25.7907 | 26.2907 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-10 | 18.8625 | 26.1817 | 25.2009 | 24.5 | 25 | 25.5 | 25.7009 | 26.2009 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-11 | 19.5167 | 25.9018 | 25.1225 | 24.5 | 25 | 25.5 | 25.6225 | 26.1225 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-12 | 21.5708 | 25.6237 | 25.0447 | 24.5 | 25 | 25.5 | 25.5447 | 26.0447 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-13 | 22.2375 | 25.4354 | 24.9919 | 24.5 | 25 | 25.5 | 25.4919 | 25.9919 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-14 | 22.825 | 25.2393 | 24.937 | 24.5 | 25 | 25.5 | 25.437 | 25.937 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-15 | 23.7583 | 25.0664 | 24.8886 | 24.5 | 25 | 25.5 | 25.3886 | 25.8886 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-16 | 24.1208 | 24.946 | 24.8549 | 24.5 | 25 | 25.5 | 25.3549 | 25.8549 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-17 | 25.2375 | 24.8493 | 24.8278 | 24.5 | 25 | 25.5 | 25.3278 | 25.8278 | 0.40969 |  | 0.7375 |  | 0.2375 |  | 0 |  | 0 |  | 0
1990-11-18 | 25.5792 | 24.8 | 24.814 | 24.5 | 25 | 25.5 | 25.314 | 25.814 | 0.76517 |  | 1.0792 |  | 0.57917 |  | 0.079167 |  | 0.26517 |  | 0
1990-11-19 | 25.0042 | 24.7496 | 24.7999 | 24.5 | 25 | 25.5 | 25.2999 | 25.7999 | 0.20428 |  | 0.50417 |  | 0.0041667 |  | 0 |  | 0 |  | 0
1990-11-20 | 23.0458 | 24.684 | 24.7815 | 24.5 | 25 | 25.5 | 25.2815 | 25.7815 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-21 | 22.2125 | 24.5587 | 24.7464 | 24.5 | 25 | 25.5 | 25.2464 | 25.7464 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-22 | 21.5542 | 24.3889 | 24.6989 | 24.5 | 25 | 25.5 | 25.1989 | 25.6989 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-23 | 20.9042 | 24.1753 | 24.6391 | 24.5 | 25 | 25.5 | 25.1391 | 25.6391 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-24 | 21.2083 | 23.9367 | 24.5723 | 24.5 | 25 | 25.5 | 25.0723 | 25.5723 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-25 | 21.0875 | 23.7018 | 24.5065 | 24.5 | 25 | 25.5 | 25.0065 | 25.5065 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-26 | 21.3125 | 23.4554 | 24.4375 | 24.5 | 25 | 25.5 | 24.9375 | 25.4375 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-27 | 19.9542 | 23.2468 | 24.3791 | 24.5 | 25 | 25.5 | 24.8791 | 25.3791 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-28 | 18.9583 | 23.0306 | 24.3186 | 24.5 | 25 | 25.5 | 24.8186 | 25.3186 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-29 | 19.2542 | 22.7999 | 24.254 | 24.5 | 25 | 25.5 | 24.754 | 25.254 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-30 | 20.1292 | 22.5711 | 24.1899 | 24.5 | 25 | 25.5 | 24.6899 | 25.1899 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-01 | 18.3292 | 22.4089 | 24.1445 | 24.5 | 25 | 25.5 | 24.6445 | 25.1445 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-02 | 18.4083 | 22.1914 | 24.0836 | 24.5 | 25 | 25.5 | 24.5836 | 25.0836 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-03 | 19.45 | 21.9688 | 24.0213 | 24.5 | 25 | 25.5 | 24.5213 | 25.0213 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-04 | 19.4417 | 21.7714 | 23.966 | 24.5 | 25 | 25.5 | 24.466 | 24.966 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-05 | 19.5792 | 21.6044 | 23.9192 | 24.5 | 25 | 25.5 | 24.4192 | 24.9192 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-06 | 19.6625 | 21.4236 | 23.8686 | 24.5 | 25 | 25.5 | 24.3686 | 24.8686 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-07 | 17.8542 | 21.2396 | 23.8171 | 24.5 | 25 | 25.5 | 24.3171 | 24.8171 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-08 | 17.4208 | 20.999 | 23.7497 | 24.5 | 25 | 25.5 | 24.2497 | 24.7497 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-09 | 17.2625 | 20.9188 | 23.7273 | 24.5 | 25 | 25.5 | 24.2273 | 24.7273 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-10 | 17.6333 | 20.8581 | 23.7103 | 24.5 | 25 | 25.5 | 24.2103 | 24.7103 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-11 | 17.3042 | 20.8171 | 23.6988 | 24.5 | 25 | 25.5 | 24.1988 | 24.6988 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-12 | 17.6667 | 20.7433 | 23.6781 | 24.5 | 25 | 25.5 | 24.1781 | 24.6781 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-13 | 18.525 | 20.6132 | 23.6417 | 24.5 | 25 | 25.5 | 24.1417 | 24.6417 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-14 | 17.9542 | 20.4894 | 23.607 | 24.5 | 25 | 25.5 | 24.107 | 24.607 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-15 | 17.8458 | 20.3271 | 23.5616 | 24.5 | 25 | 25.5 | 24.0616 | 24.5616 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-16 | 18.1542 | 20.13 | 23.5064 | 24.5 | 25 | 25.5 | 24.0064 | 24.5064 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-17 | 18.0083 | 19.9311 | 23.4507 | 24.5 | 25 | 25.5 | 23.9507 | 24.4507 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-18 | 18.0875 | 19.6901 | 23.3832 | 24.5 | 25 | 25.5 | 23.8832 | 24.3832 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-19 | 18.7625 | 19.4404 | 23.3133 | 24.5 | 25 | 25.5 | 23.8133 | 24.3133 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-20 | 16.8792 | 19.2324 | 23.2551 | 24.5 | 25 | 25.5 | 23.7551 | 24.2551 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-21 | 16.7167 | 19.0268 | 23.1975 | 24.5 | 25 | 25.5 | 23.6975 | 24.1975 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-22 | 17.35 | 18.8436 | 23.1462 | 24.5 | 25 | 25.5 | 23.6462 | 24.1462 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-23 | 17.8375 | 18.7035 | 23.107 | 24.5 | 25 | 25.5 | 23.607 | 24.107 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-24 | 17.9208 | 18.6013 | 23.0784 | 24.5 | 25 | 25.5 | 23.5784 | 24.0784 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-25 | 18.7667 | 18.4917 | 23.0477 | 24.5 | 25 | 25.5 | 23.5477 | 24.0477 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-26 | 17.4333 | 18.4143 | 23.026 | 24.5 | 25 | 25.5 | 23.526 | 24.026 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-27 | 18.3333 | 18.285 | 22.9898 | 24.5 | 25 | 25.5 | 23.4898 | 23.9898 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-28 | 20.5 | 18.231 | 22.9747 | 24.5 | 25 | 25.5 | 23.4747 | 23.9747 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-29 | 20.6167 | 18.2824 | 22.9891 | 24.5 | 25 | 25.5 | 23.4891 | 23.9891 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-30 | 19.4208 | 18.3278 | 23.0018 | 24.5 | 25 | 25.5 | 23.5018 | 24.0018 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-31 | 19.8833 | 18.3042 | 22.9952 | 24.5 | 25 | 25.5 | 23.4952 | 23.9952 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## Gwalior
Date | Daywise mean temperature | Running mean temperature (RMT) | Neutral temperature_IMAC | Baseline temperature calculated from PMV model | Plant adjusted I (Baseline + 0.5°C) | Plant adjusted II (Baseline + 1°C) | Plant adjusted I+ IMAC | Plant adjusted II+ IMAC | ACDD based on IMAC neutral temperature | 940.1656 | ACDD based on baseline temperature i.e. 24.5 calculated from the PMV model | 1323.7917 | ACDD based on 0.5°C adjustment on baseline temperature because of plant | 1219.025 | ACDD based on 1°C adjustment on baseline temperature because of plant | 1116.6333 | ACDD based on IMAC neutral temperature considering 0.5°C plant effect | 839.6666 | ACDD based on IMAC neutral temperature considering 1°C plant effect | 743.3735
1990-01-01 | 13.3125 | 14.3162 | 21.8786 | 24.5 | 25 | 25.5 | 22.3786 | 22.8786 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-02 | 13.2417 | 14.2222 | 21.8522 | 24.5 | 25 | 25.5 | 22.3522 | 22.8522 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-03 | 13.8458 | 14.1278 | 21.8258 | 24.5 | 25 | 25.5 | 22.3258 | 22.8258 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-04 | 14.7125 | 14.0585 | 21.8064 | 24.5 | 25 | 25.5 | 22.3064 | 22.8064 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-05 | 16.8167 | 14.0185 | 21.7952 | 24.5 | 25 | 25.5 | 22.2952 | 22.7952 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-06 | 15.1875 | 14.0457 | 21.8028 | 24.5 | 25 | 25.5 | 22.3028 | 22.8028 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-07 | 16.1833 | 14.0149 | 21.7942 | 24.5 | 25 | 25.5 | 22.2942 | 22.7942 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-08 | 16.575 | 14.0071 | 21.792 | 24.5 | 25 | 25.5 | 22.292 | 22.792 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-09 | 17.1042 | 14.0111 | 21.7931 | 24.5 | 25 | 25.5 | 22.2931 | 22.7931 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-10 | 17.2125 | 14.0371 | 21.8004 | 24.5 | 25 | 25.5 | 22.3004 | 22.8004 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-11 | 16.2208 | 14.0597 | 21.8067 | 24.5 | 25 | 25.5 | 22.3067 | 22.8067 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-12 | 15.5125 | 13.9889 | 21.7869 | 24.5 | 25 | 25.5 | 22.2869 | 22.7869 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-13 | 16.35 | 13.8397 | 21.7451 | 24.5 | 25 | 25.5 | 22.2451 | 22.7451 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-14 | 15.0458 | 13.904 | 21.7631 | 24.5 | 25 | 25.5 | 22.2631 | 22.7631 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-15 | 14.8 | 13.9847 | 21.7857 | 24.5 | 25 | 25.5 | 22.2857 | 22.7857 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-16 | 14.225 | 14.0985 | 21.8176 | 24.5 | 25 | 25.5 | 22.3176 | 22.8176 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-17 | 15.2542 | 14.1267 | 21.8255 | 24.5 | 25 | 25.5 | 22.3255 | 22.8255 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-18 | 13.5 | 14.1349 | 21.8278 | 24.5 | 25 | 25.5 | 22.3278 | 22.8278 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-19 | 12.5958 | 14.1294 | 21.8262 | 24.5 | 25 | 25.5 | 22.3262 | 22.8262 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-20 | 12.7417 | 14.1583 | 21.8343 | 24.5 | 25 | 25.5 | 22.3343 | 22.8343 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-21 | 13.1708 | 14.195 | 21.8446 | 24.5 | 25 | 25.5 | 22.3446 | 22.8446 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-22 | 13.15 | 14.2253 | 21.8531 | 24.5 | 25 | 25.5 | 22.3531 | 22.8531 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-23 | 13.05 | 14.2771 | 21.8676 | 24.5 | 25 | 25.5 | 22.3676 | 22.8676 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-24 | 13.225 | 14.3117 | 21.8773 | 24.5 | 25 | 25.5 | 22.3773 | 22.8773 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-25 | 13.2625 | 14.3551 | 21.8894 | 24.5 | 25 | 25.5 | 22.3894 | 22.8894 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-26 | 13.6417 | 14.3512 | 21.8883 | 24.5 | 25 | 25.5 | 22.3883 | 22.8883 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-27 | 13.475 | 14.3665 | 21.8926 | 24.5 | 25 | 25.5 | 22.3926 | 22.8926 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-28 | 14.7 | 14.3856 | 21.898 | 24.5 | 25 | 25.5 | 22.398 | 22.898 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-29 | 15.8667 | 14.4336 | 21.9114 | 24.5 | 25 | 25.5 | 22.4114 | 22.9114 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-30 | 16.5208 | 14.5293 | 21.9382 | 24.5 | 25 | 25.5 | 22.4382 | 22.9382 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-31 | 16.7333 | 14.6833 | 21.9813 | 24.5 | 25 | 25.5 | 22.4813 | 22.9813 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-01 | 18.125 | 14.7974 | 22.0133 | 24.5 | 25 | 25.5 | 22.5133 | 23.0133 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-02 | 16.3167 | 14.9601 | 22.0588 | 24.5 | 25 | 25.5 | 22.5588 | 23.0588 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-03 | 17.4833 | 15.0425 | 22.0819 | 24.5 | 25 | 25.5 | 22.5819 | 23.0819 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-04 | 15.7417 | 15.1349 | 22.1078 | 24.5 | 25 | 25.5 | 22.6078 | 23.1078 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-05 | 17.2458 | 15.099 | 22.0977 | 24.5 | 25 | 25.5 | 22.5977 | 23.0977 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-06 | 18.725 | 15.1676 | 22.1169 | 24.5 | 25 | 25.5 | 22.6169 | 23.1169 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-07 | 18.9417 | 15.2524 | 22.1407 | 24.5 | 25 | 25.5 | 22.6407 | 23.1407 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-08 | 19.3792 | 15.3313 | 22.1628 | 24.5 | 25 | 25.5 | 22.6628 | 23.1628 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-09 | 19.6625 | 15.4071 | 22.184 | 24.5 | 25 | 25.5 | 22.684 | 23.184 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-10 | 22.65 | 15.4888 | 22.2069 | 24.5 | 25 | 25.5 | 22.7069 | 23.2069 | 0.44315 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-11 | 20.9875 | 15.7031 | 22.2669 | 24.5 | 25 | 25.5 | 22.7669 | 23.2669 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-12 | 19.4875 | 15.8856 | 22.318 | 24.5 | 25 | 25.5 | 22.818 | 23.318 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-13 | 18.5667 | 15.9901 | 22.3472 | 24.5 | 25 | 25.5 | 22.8472 | 23.3472 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-14 | 17.2167 | 16.1075 | 22.3801 | 24.5 | 25 | 25.5 | 22.8801 | 23.3801 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-15 | 17.1375 | 16.1881 | 22.4027 | 24.5 | 25 | 25.5 | 22.9027 | 23.4027 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-16 | 16.9792 | 16.2851 | 22.4298 | 24.5 | 25 | 25.5 | 22.9298 | 23.4298 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-17 | 14.9542 | 16.3426 | 22.4459 | 24.5 | 25 | 25.5 | 22.9459 | 23.4459 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-18 | 15.4458 | 16.3911 | 22.4595 | 24.5 | 25 | 25.5 | 22.9595 | 23.4595 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-19 | 16.2417 | 16.4861 | 22.4861 | 24.5 | 25 | 25.5 | 22.9861 | 23.4861 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-20 | 16.7542 | 16.6028 | 22.5188 | 24.5 | 25 | 25.5 | 23.0188 | 23.5188 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-21 | 18.6667 | 16.7222 | 22.5522 | 24.5 | 25 | 25.5 | 23.0522 | 23.5522 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-22 | 20.9917 | 16.9061 | 22.6037 | 24.5 | 25 | 25.5 | 23.1037 | 23.6037 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-23 | 20.35 | 17.1708 | 22.6778 | 24.5 | 25 | 25.5 | 23.1778 | 23.6778 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-24 | 21.7042 | 17.4083 | 22.7443 | 24.5 | 25 | 25.5 | 23.2443 | 23.7443 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-25 | 22.0458 | 17.6897 | 22.8231 | 24.5 | 25 | 25.5 | 23.3231 | 23.8231 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-26 | 21.775 | 17.9699 | 22.9016 | 24.5 | 25 | 25.5 | 23.4016 | 23.9016 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-27 | 19.4125 | 18.2465 | 22.979 | 24.5 | 25 | 25.5 | 23.479 | 23.979 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-28 | 20.3208 | 18.4036 | 23.023 | 24.5 | 25 | 25.5 | 23.523 | 24.023 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-01 | 19.7958 | 18.5521 | 23.0646 | 24.5 | 25 | 25.5 | 23.5646 | 24.0646 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-02 | 20.7083 | 18.6613 | 23.0952 | 24.5 | 25 | 25.5 | 23.5952 | 24.0952 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-03 | 21.75 | 18.7938 | 23.1323 | 24.5 | 25 | 25.5 | 23.6323 | 24.1323 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-04 | 22.5167 | 18.9146 | 23.1661 | 24.5 | 25 | 25.5 | 23.6661 | 24.1661 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-05 | 22.2958 | 19.1213 | 23.224 | 24.5 | 25 | 25.5 | 23.724 | 24.224 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-06 | 20.9 | 19.2817 | 23.2689 | 24.5 | 25 | 25.5 | 23.7689 | 24.2689 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-07 | 19.5542 | 19.4536 | 23.317 | 24.5 | 25 | 25.5 | 23.817 | 24.317 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-08 | 21.5042 | 19.5306 | 23.3386 | 24.5 | 25 | 25.5 | 23.8386 | 24.3386 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-09 | 22.6833 | 19.6232 | 23.3645 | 24.5 | 25 | 25.5 | 23.8645 | 24.3645 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-10 | 23.6542 | 19.7479 | 23.3994 | 24.5 | 25 | 25.5 | 23.8994 | 24.3994 | 0.25475 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-11 | 23.7708 | 19.8904 | 23.4393 | 24.5 | 25 | 25.5 | 23.9393 | 24.4393 | 0.33152 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-12 | 24.7625 | 20.0274 | 23.4777 | 24.5 | 25 | 25.5 | 23.9777 | 24.4777 | 1.2848 |  | 0.2625 |  | 0 |  | 0 |  | 0.78484 |  | 0.28484
1990-03-13 | 25.225 | 20.0978 | 23.4974 | 24.5 | 25 | 25.5 | 23.9974 | 24.4974 | 1.7276 |  | 0.725 |  | 0.225 |  | 0 |  | 1.2276 |  | 0.72762
1990-03-14 | 23.2375 | 20.239 | 23.5369 | 24.5 | 25 | 25.5 | 24.0369 | 24.5369 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-15 | 23.7875 | 20.364 | 23.5719 | 24.5 | 25 | 25.5 | 24.0719 | 24.5719 | 0.21557 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-16 | 24.475 | 20.5381 | 23.6207 | 24.5 | 25 | 25.5 | 24.1207 | 24.6207 | 0.85434 |  | 0 |  | 0 |  | 0 |  | 0.35434 |  | 0
1990-03-17 | 24.1792 | 20.78 | 23.6884 | 24.5 | 25 | 25.5 | 24.1884 | 24.6884 | 0.49077 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-18 | 27.2458 | 21.0147 | 23.7541 | 24.5 | 25 | 25.5 | 24.2541 | 24.7541 | 3.4917 |  | 2.7458 |  | 2.2458 |  | 1.7458 |  | 2.9917 |  | 2.4917
1990-03-19 | 26.5625 | 21.3569 | 23.8499 | 24.5 | 25 | 25.5 | 24.3499 | 24.8499 | 2.7126 |  | 2.0625 |  | 1.5625 |  | 1.0625 |  | 2.2126 |  | 1.7126
1990-03-20 | 24.1875 | 21.7439 | 23.9583 | 24.5 | 25 | 25.5 | 24.4583 | 24.9583 | 0.22921 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-21 | 26.1167 | 22.0353 | 24.0399 | 24.5 | 25 | 25.5 | 24.5399 | 25.0399 | 2.0768 |  | 1.6167 |  | 1.1167 |  | 0.61667 |  | 1.5768 |  | 1.0768
1990-03-22 | 25.875 | 22.3644 | 24.132 | 24.5 | 25 | 25.5 | 24.632 | 25.132 | 1.743 |  | 1.375 |  | 0.875 |  | 0.375 |  | 1.243 |  | 0.74296
1990-03-23 | 24.3667 | 22.6685 | 24.2172 | 24.5 | 25 | 25.5 | 24.7172 | 25.2172 | 0.14949 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-24 | 23.2042 | 22.8585 | 24.2704 | 24.5 | 25 | 25.5 | 24.7704 | 25.2704 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-25 | 23.6625 | 22.9322 | 24.291 | 24.5 | 25 | 25.5 | 24.791 | 25.291 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-26 | 24.4292 | 23.0426 | 24.3219 | 24.5 | 25 | 25.5 | 24.8219 | 25.3219 | 0.10723 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-27 | 25.8833 | 23.1335 | 24.3474 | 24.5 | 25 | 25.5 | 24.8474 | 25.3474 | 1.536 |  | 1.3833 |  | 0.88333 |  | 0.38333 |  | 1.036 |  | 0.53596
1990-03-28 | 26.1083 | 23.2614 | 24.3832 | 24.5 | 25 | 25.5 | 24.8832 | 25.3832 | 1.7251 |  | 1.6083 |  | 1.1083 |  | 0.60833 |  | 1.2251 |  | 0.72514
1990-03-29 | 27.1958 | 23.4058 | 24.4236 | 24.5 | 25 | 25.5 | 24.9236 | 25.4236 | 2.7722 |  | 2.6958 |  | 2.1958 |  | 1.6958 |  | 2.2722 |  | 1.7722
1990-03-30 | 29.0833 | 23.6653 | 24.4963 | 24.5 | 25 | 25.5 | 24.9963 | 25.4963 | 4.5871 |  | 4.5833 |  | 4.0833 |  | 3.5833 |  | 4.0871 |  | 3.5871
1990-03-31 | 30.1 | 23.9574 | 24.5781 | 24.5 | 25 | 25.5 | 25.0781 | 25.5781 | 5.5219 |  | 5.6 |  | 5.1 |  | 4.6 |  | 5.0219 |  | 4.5219
1990-04-01 | 26.475 | 24.3008 | 24.6742 | 24.5 | 25 | 25.5 | 25.1742 | 25.6742 | 1.8008 |  | 1.975 |  | 1.475 |  | 0.975 |  | 1.3008 |  | 0.80077
1990-04-02 | 28.4208 | 24.4931 | 24.7281 | 24.5 | 25 | 25.5 | 25.2281 | 25.7281 | 3.6928 |  | 3.9208 |  | 3.4208 |  | 2.9208 |  | 3.1928 |  | 2.6928
1990-04-03 | 25.5333 | 24.7154 | 24.7903 | 24.5 | 25 | 25.5 | 25.2903 | 25.7903 | 0.74302 |  | 1.0333 |  | 0.53333 |  | 0.033333 |  | 0.24302 |  | 0
1990-04-04 | 24.0708 | 24.816 | 24.8185 | 24.5 | 25 | 25.5 | 25.3185 | 25.8185 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-04-05 | 24.5875 | 24.8751 | 24.835 | 24.5 | 25 | 25.5 | 25.335 | 25.835 | 0 |  | 0.0875 |  | 0 |  | 0 |  | 0 |  | 0
1990-04-06 | 25.4667 | 24.9981 | 24.8695 | 24.5 | 25 | 25.5 | 25.3695 | 25.8695 | 0.59721 |  | 0.96667 |  | 0.46667 |  | 0 |  | 0.097211 |  | 0
1990-04-07 | 28.0208 | 25.1951 | 24.9246 | 24.5 | 25 | 25.5 | 25.4246 | 25.9246 | 3.0962 |  | 3.5208 |  | 3.0208 |  | 2.5208 |  | 2.5962 |  | 2.0962
1990-04-08 | 28.6958 | 25.4124 | 24.9855 | 24.5 | 25 | 25.5 | 25.4855 | 25.9855 | 3.7104 |  | 4.1958 |  | 3.6958 |  | 3.1958 |  | 3.2104 |  | 2.7104
1990-04-09 | 29.8 | 25.6128 | 25.0416 | 24.5 | 25 | 25.5 | 25.5416 | 26.0416 | 4.7584 |  | 5.3 |  | 4.8 |  | 4.3 |  | 4.2584 |  | 3.7584
1990-04-10 | 30.4875 | 25.8176 | 25.0989 | 24.5 | 25 | 25.5 | 25.5989 | 26.0989 | 5.3886 |  | 5.9875 |  | 5.4875 |  | 4.9875 |  | 4.8886 |  | 4.3886
1990-04-11 | 30.0833 | 26.0415 | 25.1616 | 24.5 | 25 | 25.5 | 25.6616 | 26.1616 | 4.9217 |  | 5.5833 |  | 5.0833 |  | 4.5833 |  | 4.4217 |  | 3.9217
1990-04-12 | 31.9 | 26.2189 | 25.2113 | 24.5 | 25 | 25.5 | 25.7113 | 26.2113 | 6.6887 |  | 7.4 |  | 6.9 |  | 6.4 |  | 6.1887 |  | 5.6887
1990-04-13 | 30.8375 | 26.4414 | 25.2736 | 24.5 | 25 | 25.5 | 25.7736 | 26.2736 | 5.5639 |  | 6.3375 |  | 5.8375 |  | 5.3375 |  | 5.0639 |  | 4.5639
1990-04-14 | 31.05 | 26.6947 | 25.3445 | 24.5 | 25 | 25.5 | 25.8445 | 26.3445 | 5.7055 |  | 6.55 |  | 6.05 |  | 5.55 |  | 5.2055 |  | 4.7055
1990-04-15 | 30.85 | 26.9368 | 25.4123 | 24.5 | 25 | 25.5 | 25.9123 | 26.4123 | 5.4377 |  | 6.35 |  | 5.85 |  | 5.35 |  | 4.9377 |  | 4.4377
1990-04-16 | 31.0292 | 27.1493 | 25.4718 | 24.5 | 25 | 25.5 | 25.9718 | 26.4718 | 5.5574 |  | 6.5292 |  | 6.0292 |  | 5.5292 |  | 5.0574 |  | 4.5574
1990-04-17 | 30.6917 | 27.3776 | 25.5357 | 24.5 | 25 | 25.5 | 26.0357 | 26.5357 | 5.1559 |  | 6.1917 |  | 5.6917 |  | 5.1917 |  | 4.6559 |  | 4.1559
1990-04-18 | 30.7958 | 27.4925 | 25.5679 | 24.5 | 25 | 25.5 | 26.0679 | 26.5679 | 5.2279 |  | 6.2958 |  | 5.7958 |  | 5.2958 |  | 4.7279 |  | 4.2279
1990-04-19 | 31.1375 | 27.6336 | 25.6074 | 24.5 | 25 | 25.5 | 26.1074 | 26.6074 | 5.5301 |  | 6.6375 |  | 6.1375 |  | 5.6375 |  | 5.0301 |  | 4.5301
1990-04-20 | 31.1083 | 27.8653 | 25.6723 | 24.5 | 25 | 25.5 | 26.1723 | 26.6723 | 5.4361 |  | 6.6083 |  | 6.1083 |  | 5.6083 |  | 4.9361 |  | 4.4361
1990-04-21 | 31.7833 | 28.0317 | 25.7189 | 24.5 | 25 | 25.5 | 26.2189 | 26.7189 | 6.0645 |  | 7.2833 |  | 6.7833 |  | 6.2833 |  | 5.5645 |  | 5.0645
1990-04-22 | 32.425 | 28.2286 | 25.774 | 24.5 | 25 | 25.5 | 26.274 | 26.774 | 6.651 |  | 7.925 |  | 7.425 |  | 6.925 |  | 6.151 |  | 5.651
1990-04-23 | 32.5833 | 28.4972 | 25.8492 | 24.5 | 25 | 25.5 | 26.3492 | 26.8492 | 6.7341 |  | 8.0833 |  | 7.5833 |  | 7.0833 |  | 6.2341 |  | 5.7341
1990-04-24 | 33.3625 | 28.8099 | 25.9368 | 24.5 | 25 | 25.5 | 26.4368 | 26.9368 | 7.4257 |  | 8.8625 |  | 8.3625 |  | 7.8625 |  | 6.9257 |  | 6.4257
1990-04-25 | 34.2708 | 29.1332 | 26.0273 | 24.5 | 25 | 25.5 | 26.5273 | 27.0273 | 8.2435 |  | 9.7708 |  | 9.2708 |  | 8.7708 |  | 7.7435 |  | 7.2435
1990-04-26 | 33.4125 | 29.4612 | 26.1191 | 24.5 | 25 | 25.5 | 26.6191 | 27.1191 | 7.2934 |  | 8.9125 |  | 8.4125 |  | 7.9125 |  | 6.7934 |  | 6.2934
1990-04-27 | 32.525 | 29.7122 | 26.1894 | 24.5 | 25 | 25.5 | 26.6894 | 27.1894 | 6.3356 |  | 8.025 |  | 7.525 |  | 7.025 |  | 5.8356 |  | 5.3356
1990-04-28 | 30.7917 | 29.9261 | 26.2493 | 24.5 | 25 | 25.5 | 26.7493 | 27.2493 | 4.5424 |  | 6.2917 |  | 5.7917 |  | 5.2917 |  | 4.0424 |  | 3.5424
1990-04-29 | 30.6 | 30.046 | 26.2829 | 24.5 | 25 | 25.5 | 26.7829 | 27.2829 | 4.3171 |  | 6.1 |  | 5.6 |  | 5.1 |  | 3.8171 |  | 3.3171
1990-04-30 | 30.7208 | 30.0965 | 26.297 | 24.5 | 25 | 25.5 | 26.797 | 27.297 | 4.4238 |  | 6.2208 |  | 5.7208 |  | 5.2208 |  | 3.9238 |  | 3.4238
1990-05-01 | 34.4542 | 30.1172 | 26.3028 | 24.5 | 25 | 25.5 | 26.8028 | 27.3028 | 8.1513 |  | 9.9542 |  | 9.4542 |  | 8.9542 |  | 7.6513 |  | 7.1513
1990-05-02 | 32.1208 | 30.3832 | 26.3773 | 24.5 | 25 | 25.5 | 26.8773 | 27.3773 | 5.7435 |  | 7.6208 |  | 7.1208 |  | 6.6208 |  | 5.2435 |  | 4.7435
1990-05-03 | 32.5417 | 30.5065 | 26.4118 | 24.5 | 25 | 25.5 | 26.9118 | 27.4118 | 6.1298 |  | 8.0417 |  | 7.5417 |  | 7.0417 |  | 5.6298 |  | 5.1298
1990-05-04 | 30.9958 | 30.7401 | 26.4772 | 24.5 | 25 | 25.5 | 26.9772 | 27.4772 | 4.5186 |  | 6.4958 |  | 5.9958 |  | 5.4958 |  | 4.0186 |  | 3.5186
1990-05-05 | 25.2583 | 30.971 | 26.5419 | 24.5 | 25 | 25.5 | 27.0419 | 27.5419 | 0 |  | 0.75833 |  | 0.25833 |  | 0 |  | 0 |  | 0
1990-05-06 | 28.3833 | 30.9933 | 26.5481 | 24.5 | 25 | 25.5 | 27.0481 | 27.5481 | 1.8352 |  | 3.8833 |  | 3.3833 |  | 2.8833 |  | 1.3352 |  | 0.8352
1990-05-07 | 29.3583 | 31.0906 | 26.5754 | 24.5 | 25 | 25.5 | 27.0754 | 27.5754 | 2.783 |  | 4.8583 |  | 4.3583 |  | 3.8583 |  | 2.283 |  | 1.783
1990-05-08 | 32.3625 | 31.1351 | 26.5878 | 24.5 | 25 | 25.5 | 27.0878 | 27.5878 | 5.7747 |  | 7.8625 |  | 7.3625 |  | 6.8625 |  | 5.2747 |  | 4.7747
1990-05-09 | 33.7208 | 31.2574 | 26.6221 | 24.5 | 25 | 25.5 | 27.1221 | 27.6221 | 7.0988 |  | 9.2208 |  | 8.7208 |  | 8.2208 |  | 6.5988 |  | 6.0988
1990-05-10 | 35.2708 | 31.3881 | 26.6587 | 24.5 | 25 | 25.5 | 27.1587 | 27.6587 | 8.6122 |  | 10.7708 |  | 10.2708 |  | 9.7708 |  | 8.1122 |  | 7.6122
1990-05-11 | 34.2125 | 31.5475 | 26.7033 | 24.5 | 25 | 25.5 | 27.2033 | 27.7033 | 7.5092 |  | 9.7125 |  | 9.2125 |  | 8.7125 |  | 7.0092 |  | 6.5092
1990-05-12 | 33.1083 | 31.6851 | 26.7418 | 24.5 | 25 | 25.5 | 27.2418 | 27.7418 | 6.3665 |  | 8.6083 |  | 8.1083 |  | 7.6083 |  | 5.8665 |  | 5.3665
1990-05-13 | 31.1833 | 31.7254 | 26.7531 | 24.5 | 25 | 25.5 | 27.2531 | 27.7531 | 4.4302 |  | 6.6833 |  | 6.1833 |  | 5.6833 |  | 3.9302 |  | 3.4302
1990-05-14 | 34.475 | 31.7369 | 26.7563 | 24.5 | 25 | 25.5 | 27.2563 | 27.7563 | 7.7187 |  | 9.975 |  | 9.475 |  | 8.975 |  | 7.2187 |  | 6.7187
1990-05-15 | 35.125 | 31.8511 | 26.7883 | 24.5 | 25 | 25.5 | 27.2883 | 27.7883 | 8.3367 |  | 10.625 |  | 10.125 |  | 9.625 |  | 7.8367 |  | 7.3367
1990-05-16 | 35.6542 | 31.9936 | 26.8282 | 24.5 | 25 | 25.5 | 27.3282 | 27.8282 | 8.826 |  | 11.1542 |  | 10.6542 |  | 10.1542 |  | 8.326 |  | 7.826
1990-05-17 | 36.6792 | 32.1478 | 26.8714 | 24.5 | 25 | 25.5 | 27.3714 | 27.8714 | 9.8078 |  | 12.1792 |  | 11.6792 |  | 11.1792 |  | 9.3078 |  | 8.8078
1990-05-18 | 33.2833 | 32.3474 | 26.9273 | 24.5 | 25 | 25.5 | 27.4273 | 27.9273 | 6.3561 |  | 8.7833 |  | 8.2833 |  | 7.7833 |  | 5.8561 |  | 5.3561
1990-05-19 | 34.8625 | 32.4303 | 26.9505 | 24.5 | 25 | 25.5 | 27.4505 | 27.9505 | 7.912 |  | 10.3625 |  | 9.8625 |  | 9.3625 |  | 7.412 |  | 6.912
1990-05-20 | 34.3542 | 32.5544 | 26.9852 | 24.5 | 25 | 25.5 | 27.4852 | 27.9852 | 7.3689 |  | 9.8542 |  | 9.3542 |  | 8.8542 |  | 6.8689 |  | 6.3689
1990-05-21 | 36.9083 | 32.6626 | 27.0155 | 24.5 | 25 | 25.5 | 27.5155 | 28.0155 | 9.8928 |  | 12.4083 |  | 11.9083 |  | 11.4083 |  | 9.3928 |  | 8.8928
1990-05-22 | 36.3208 | 32.8335 | 27.0634 | 24.5 | 25 | 25.5 | 27.5634 | 28.0634 | 9.2575 |  | 11.8208 |  | 11.3208 |  | 10.8208 |  | 8.7575 |  | 8.2575
1990-05-23 | 37.1583 | 32.9633 | 27.0997 | 24.5 | 25 | 25.5 | 27.5997 | 28.0997 | 10.0586 |  | 12.6583 |  | 12.1583 |  | 11.6583 |  | 9.5586 |  | 9.0586
1990-05-24 | 36.1458 | 33.1158 | 27.1424 | 24.5 | 25 | 25.5 | 27.6424 | 28.1424 | 9.0034 |  | 11.6458 |  | 11.1458 |  | 10.6458 |  | 8.5034 |  | 8.0034
1990-05-25 | 38.0208 | 33.2086 | 27.1684 | 24.5 | 25 | 25.5 | 27.6684 | 28.1684 | 10.8524 |  | 13.5208 |  | 13.0208 |  | 12.5208 |  | 10.3524 |  | 9.8524
1990-05-26 | 34.6167 | 33.3336 | 27.2034 | 24.5 | 25 | 25.5 | 27.7034 | 28.2034 | 7.4133 |  | 10.1167 |  | 9.6167 |  | 9.1167 |  | 6.9133 |  | 6.4133
1990-05-27 | 37.4042 | 33.3737 | 27.2146 | 24.5 | 25 | 25.5 | 27.7146 | 28.2146 | 10.1895 |  | 12.9042 |  | 12.4042 |  | 11.9042 |  | 9.6895 |  | 9.1895
1990-05-28 | 37.3625 | 33.5364 | 27.2602 | 24.5 | 25 | 25.5 | 27.7602 | 28.2602 | 10.1023 |  | 12.8625 |  | 12.3625 |  | 11.8625 |  | 9.6023 |  | 9.1023
1990-05-29 | 37.7417 | 33.7554 | 27.3215 | 24.5 | 25 | 25.5 | 27.8215 | 28.3215 | 10.4202 |  | 13.2417 |  | 12.7417 |  | 12.2417 |  | 9.9202 |  | 9.4202
1990-05-30 | 34.7042 | 33.9935 | 27.3882 | 24.5 | 25 | 25.5 | 27.8882 | 28.3882 | 7.316 |  | 10.2042 |  | 9.7042 |  | 9.2042 |  | 6.816 |  | 6.316
1990-05-31 | 33.55 | 34.1262 | 27.4253 | 24.5 | 25 | 25.5 | 27.9253 | 28.4253 | 6.1246 |  | 9.05 |  | 8.55 |  | 8.05 |  | 5.6246 |  | 5.1246
1990-06-01 | 38.8292 | 34.0961 | 27.4169 | 24.5 | 25 | 25.5 | 27.9169 | 28.4169 | 11.4123 |  | 14.3292 |  | 13.8292 |  | 13.3292 |  | 10.9123 |  | 10.4123
1990-06-02 | 37.4625 | 34.3197 | 27.4795 | 24.5 | 25 | 25.5 | 27.9795 | 28.4795 | 9.983 |  | 12.9625 |  | 12.4625 |  | 11.9625 |  | 9.483 |  | 8.983
1990-06-03 | 37.3625 | 34.4837 | 27.5254 | 24.5 | 25 | 25.5 | 28.0254 | 28.5254 | 9.837 |  | 12.8625 |  | 12.3625 |  | 11.8625 |  | 9.337 |  | 8.837
1990-06-04 | 37.7208 | 34.696 | 27.5849 | 24.5 | 25 | 25.5 | 28.0849 | 28.5849 | 10.136 |  | 13.2208 |  | 12.7208 |  | 12.2208 |  | 9.636 |  | 9.136
1990-06-05 | 34.7667 | 35.1114 | 27.7012 | 24.5 | 25 | 25.5 | 28.2012 | 28.7012 | 7.0655 |  | 10.2667 |  | 9.7667 |  | 9.2667 |  | 6.5655 |  | 6.0655
1990-06-06 | 31.3125 | 35.3242 | 27.7608 | 24.5 | 25 | 25.5 | 28.2608 | 28.7608 | 3.5517 |  | 6.8125 |  | 6.3125 |  | 5.8125 |  | 3.0517 |  | 2.5517
1990-06-07 | 34.3333 | 35.3893 | 27.779 | 24.5 | 25 | 25.5 | 28.279 | 28.779 | 6.5543 |  | 9.8333 |  | 9.3333 |  | 8.8333 |  | 6.0543 |  | 5.5543
1990-06-08 | 35.6458 | 35.455 | 27.7974 | 24.5 | 25 | 25.5 | 28.2974 | 28.7974 | 7.8484 |  | 11.1458 |  | 10.6458 |  | 10.1458 |  | 7.3484 |  | 6.8484
1990-06-09 | 35.9167 | 35.5192 | 27.8154 | 24.5 | 25 | 25.5 | 28.3154 | 28.8154 | 8.1013 |  | 11.4167 |  | 10.9167 |  | 10.4167 |  | 7.6013 |  | 7.1013
1990-06-10 | 35.9833 | 35.5407 | 27.8214 | 24.5 | 25 | 25.5 | 28.3214 | 28.8214 | 8.1619 |  | 11.4833 |  | 10.9833 |  | 10.4833 |  | 7.6619 |  | 7.1619
1990-06-11 | 36.425 | 35.5997 | 27.8379 | 24.5 | 25 | 25.5 | 28.3379 | 28.8379 | 8.5871 |  | 11.925 |  | 11.425 |  | 10.925 |  | 8.0871 |  | 7.5871
1990-06-12 | 37.9917 | 35.7103 | 27.8689 | 24.5 | 25 | 25.5 | 28.3689 | 28.8689 | 10.1228 |  | 13.4917 |  | 12.9917 |  | 12.4917 |  | 9.6228 |  | 9.1228
1990-06-13 | 38.5667 | 35.9372 | 27.9324 | 24.5 | 25 | 25.5 | 28.4324 | 28.9324 | 10.6342 |  | 14.0667 |  | 13.5667 |  | 13.0667 |  | 10.1342 |  | 9.6342
1990-06-14 | 35.525 | 36.0736 | 27.9706 | 24.5 | 25 | 25.5 | 28.4706 | 28.9706 | 7.5544 |  | 11.025 |  | 10.525 |  | 10.025 |  | 7.0544 |  | 6.5544
1990-06-15 | 35.5375 | 36.0869 | 27.9743 | 24.5 | 25 | 25.5 | 28.4743 | 28.9743 | 7.5632 |  | 11.0375 |  | 10.5375 |  | 10.0375 |  | 7.0632 |  | 6.5632
1990-06-16 | 34.6333 | 36.0831 | 27.9733 | 24.5 | 25 | 25.5 | 28.4733 | 28.9733 | 6.6601 |  | 10.1333 |  | 9.6333 |  | 9.1333 |  | 6.1601 |  | 5.6601
1990-06-17 | 32.6 | 36.0149 | 27.9542 | 24.5 | 25 | 25.5 | 28.4542 | 28.9542 | 4.6458 |  | 8.1 |  | 7.6 |  | 7.1 |  | 4.1458 |  | 3.6458
1990-06-18 | 30.5125 | 35.9921 | 27.9478 | 24.5 | 25 | 25.5 | 28.4478 | 28.9478 | 2.5647 |  | 6.0125 |  | 5.5125 |  | 5.0125 |  | 2.0647 |  | 1.5647
1990-06-19 | 32.7083 | 35.8471 | 27.9072 | 24.5 | 25 | 25.5 | 28.4072 | 28.9072 | 4.8011 |  | 8.2083 |  | 7.7083 |  | 7.2083 |  | 4.3011 |  | 3.8011
1990-06-20 | 33.3167 | 35.7922 | 27.8918 | 24.5 | 25 | 25.5 | 28.3918 | 28.8918 | 5.4248 |  | 8.8167 |  | 8.3167 |  | 7.8167 |  | 4.9248 |  | 4.4248
1990-06-21 | 32.2708 | 35.6725 | 27.8583 | 24.5 | 25 | 25.5 | 28.3583 | 28.8583 | 4.4125 |  | 7.7708 |  | 7.2708 |  | 6.7708 |  | 3.9125 |  | 3.4125
1990-06-22 | 31.7625 | 35.5375 | 27.8205 | 24.5 | 25 | 25.5 | 28.3205 | 28.8205 | 3.942 |  | 7.2625 |  | 6.7625 |  | 6.2625 |  | 3.442 |  | 2.942
1990-06-23 | 30.4208 | 35.3576 | 27.7701 | 24.5 | 25 | 25.5 | 28.2701 | 28.7701 | 2.6507 |  | 5.9208 |  | 5.4208 |  | 4.9208 |  | 2.1507 |  | 1.6507
1990-06-24 | 31.325 | 35.1668 | 27.7167 | 24.5 | 25 | 25.5 | 28.2167 | 28.7167 | 3.6083 |  | 6.825 |  | 6.325 |  | 5.825 |  | 3.1083 |  | 2.6083
1990-06-25 | 31.3125 | 34.9436 | 27.6542 | 24.5 | 25 | 25.5 | 28.1542 | 28.6542 | 3.6583 |  | 6.8125 |  | 6.3125 |  | 5.8125 |  | 3.1583 |  | 2.6583
1990-06-26 | 31.1458 | 34.8335 | 27.6234 | 24.5 | 25 | 25.5 | 28.1234 | 28.6234 | 3.5225 |  | 6.6458 |  | 6.1458 |  | 5.6458 |  | 3.0225 |  | 2.5225
1990-06-27 | 33.9667 | 34.6249 | 27.565 | 24.5 | 25 | 25.5 | 28.065 | 28.565 | 6.4017 |  | 9.4667 |  | 8.9667 |  | 8.4667 |  | 5.9017 |  | 5.4017
1990-06-28 | 27.3375 | 34.5117 | 27.5333 | 24.5 | 25 | 25.5 | 28.0333 | 28.5333 | 0 |  | 2.8375 |  | 2.3375 |  | 1.8375 |  | 0 |  | 0
1990-06-29 | 27.3417 | 34.1649 | 27.4362 | 24.5 | 25 | 25.5 | 27.9362 | 28.4362 | 0 |  | 2.8417 |  | 2.3417 |  | 1.8417 |  | 0 |  | 0
1990-06-30 | 27.5292 | 33.9194 | 27.3674 | 24.5 | 25 | 25.5 | 27.8674 | 28.3674 | 0.16172 |  | 3.0292 |  | 2.5292 |  | 2.0292 |  | 0 |  | 0
1990-07-01 | 31.5375 | 33.7188 | 27.3113 | 24.5 | 25 | 25.5 | 27.8113 | 28.3113 | 4.2262 |  | 7.0375 |  | 6.5375 |  | 6.0375 |  | 3.7262 |  | 3.2262
1990-07-02 | 30.4625 | 33.4757 | 27.2432 | 24.5 | 25 | 25.5 | 27.7432 | 28.2432 | 3.2193 |  | 5.9625 |  | 5.4625 |  | 4.9625 |  | 2.7193 |  | 2.2193
1990-07-03 | 30.2667 | 33.2424 | 27.1779 | 24.5 | 25 | 25.5 | 27.6779 | 28.1779 | 3.0888 |  | 5.7667 |  | 5.2667 |  | 4.7667 |  | 2.5888 |  | 2.0888
1990-07-04 | 31.6833 | 33.0058 | 27.1116 | 24.5 | 25 | 25.5 | 27.6116 | 28.1116 | 4.5717 |  | 7.1833 |  | 6.6833 |  | 6.1833 |  | 4.0717 |  | 3.5717
1990-07-05 | 32.0333 | 32.8046 | 27.0553 | 24.5 | 25 | 25.5 | 27.5553 | 28.0553 | 4.978 |  | 7.5333 |  | 7.0333 |  | 6.5333 |  | 4.478 |  | 3.978
1990-07-06 | 32.6542 | 32.7135 | 27.0298 | 24.5 | 25 | 25.5 | 27.5298 | 28.0298 | 5.6244 |  | 8.1542 |  | 7.6542 |  | 7.1542 |  | 5.1244 |  | 4.6244
1990-07-07 | 31.8208 | 32.7582 | 27.0423 | 24.5 | 25 | 25.5 | 27.5423 | 28.0423 | 4.7785 |  | 7.3208 |  | 6.8208 |  | 6.3208 |  | 4.2785 |  | 3.7785
1990-07-08 | 30.2042 | 32.6744 | 27.0188 | 24.5 | 25 | 25.5 | 27.5188 | 28.0188 | 3.1853 |  | 5.7042 |  | 5.2042 |  | 4.7042 |  | 2.6853 |  | 2.1853
1990-07-09 | 30.2333 | 32.4931 | 26.9681 | 24.5 | 25 | 25.5 | 27.4681 | 27.9681 | 3.2653 |  | 5.7333 |  | 5.2333 |  | 4.7333 |  | 2.7653 |  | 2.2653
1990-07-10 | 31.825 | 32.3036 | 26.915 | 24.5 | 25 | 25.5 | 27.415 | 27.915 | 4.91 |  | 7.325 |  | 6.825 |  | 6.325 |  | 4.41 |  | 3.91
1990-07-11 | 31.6125 | 32.165 | 26.8762 | 24.5 | 25 | 25.5 | 27.3762 | 27.8762 | 4.7363 |  | 7.1125 |  | 6.6125 |  | 6.1125 |  | 4.2363 |  | 3.7363
1990-07-12 | 31.7167 | 32.0046 | 26.8313 | 24.5 | 25 | 25.5 | 27.3313 | 27.8313 | 4.8854 |  | 7.2167 |  | 6.7167 |  | 6.2167 |  | 4.3854 |  | 3.8854
1990-07-13 | 30.2875 | 31.7954 | 26.7727 | 24.5 | 25 | 25.5 | 27.2727 | 27.7727 | 3.5148 |  | 5.7875 |  | 5.2875 |  | 4.7875 |  | 3.0148 |  | 2.5148
1990-07-14 | 29.2417 | 31.5194 | 26.6954 | 24.5 | 25 | 25.5 | 27.1954 | 27.6954 | 2.5462 |  | 4.7417 |  | 4.2417 |  | 3.7417 |  | 2.0462 |  | 1.5462
1990-07-15 | 26.8958 | 31.31 | 26.6368 | 24.5 | 25 | 25.5 | 27.1368 | 27.6368 | 0.25903 |  | 2.3958 |  | 1.8958 |  | 1.3958 |  | 0 |  | 0
1990-07-16 | 30.0292 | 31.0219 | 26.5561 | 24.5 | 25 | 25.5 | 27.0561 | 27.5561 | 3.473 |  | 5.5292 |  | 5.0292 |  | 4.5292 |  | 2.973 |  | 2.473
1990-07-17 | 30.9542 | 30.8685 | 26.5132 | 24.5 | 25 | 25.5 | 27.0132 | 27.5132 | 4.441 |  | 6.4542 |  | 5.9542 |  | 5.4542 |  | 3.941 |  | 3.441
1990-07-18 | 33.9875 | 30.8136 | 26.4978 | 24.5 | 25 | 25.5 | 26.9978 | 27.4978 | 7.4897 |  | 9.4875 |  | 8.9875 |  | 8.4875 |  | 6.9897 |  | 6.4897
1990-07-19 | 35.0625 | 30.9294 | 26.5302 | 24.5 | 25 | 25.5 | 27.0302 | 27.5302 | 8.5323 |  | 10.5625 |  | 10.0625 |  | 9.5625 |  | 8.0323 |  | 7.5323
1990-07-20 | 32.9375 | 31.0079 | 26.5522 | 24.5 | 25 | 25.5 | 27.0522 | 27.5522 | 6.3853 |  | 8.4375 |  | 7.9375 |  | 7.4375 |  | 5.8853 |  | 5.3853
1990-07-21 | 28.3208 | 30.9953 | 26.5487 | 24.5 | 25 | 25.5 | 27.0487 | 27.5487 | 1.7722 |  | 3.8208 |  | 3.3208 |  | 2.8208 |  | 1.2722 |  | 0.77216
1990-07-22 | 30.5292 | 30.8636 | 26.5118 | 24.5 | 25 | 25.5 | 27.0118 | 27.5118 | 4.0174 |  | 6.0292 |  | 5.5292 |  | 5.0292 |  | 3.5174 |  | 3.0174
1990-07-23 | 31.4958 | 30.8225 | 26.5003 | 24.5 | 25 | 25.5 | 27.0003 | 27.5003 | 4.9955 |  | 6.9958 |  | 6.4958 |  | 5.9958 |  | 4.4955 |  | 3.9955
1990-07-24 | 29.925 | 30.8583 | 26.5103 | 24.5 | 25 | 25.5 | 27.0103 | 27.5103 | 3.4147 |  | 5.425 |  | 4.925 |  | 4.425 |  | 2.9147 |  | 2.4147
1990-07-25 | 30.1292 | 30.8117 | 26.4973 | 24.5 | 25 | 25.5 | 26.9973 | 27.4973 | 3.6319 |  | 5.6292 |  | 5.1292 |  | 4.6292 |  | 3.1319 |  | 2.6319
1990-07-26 | 31.5667 | 30.7722 | 26.4862 | 24.5 | 25 | 25.5 | 26.9862 | 27.4862 | 5.0804 |  | 7.0667 |  | 6.5667 |  | 6.0667 |  | 4.5804 |  | 4.0804
1990-07-27 | 31.1875 | 30.7863 | 26.4902 | 24.5 | 25 | 25.5 | 26.9902 | 27.4902 | 4.6973 |  | 6.6875 |  | 6.1875 |  | 5.6875 |  | 4.1973 |  | 3.6973
1990-07-28 | 30.625 | 30.6936 | 26.4642 | 24.5 | 25 | 25.5 | 26.9642 | 27.4642 | 4.1608 |  | 6.125 |  | 5.625 |  | 5.125 |  | 3.6608 |  | 3.1608
1990-07-29 | 28.3 | 30.8032 | 26.4949 | 24.5 | 25 | 25.5 | 26.9949 | 27.4949 | 1.8051 |  | 3.8 |  | 3.3 |  | 2.8 |  | 1.3051 |  | 0.80511
1990-07-30 | 27.9625 | 30.8351 | 26.5038 | 24.5 | 25 | 25.5 | 27.0038 | 27.5038 | 1.4587 |  | 3.4625 |  | 2.9625 |  | 2.4625 |  | 0.95866 |  | 0.45866
1990-07-31 | 29.6833 | 30.8496 | 26.5079 | 24.5 | 25 | 25.5 | 27.0079 | 27.5079 | 3.1754 |  | 5.1833 |  | 4.6833 |  | 4.1833 |  | 2.6754 |  | 2.1754
1990-08-01 | 28.9333 | 30.7878 | 26.4906 | 24.5 | 25 | 25.5 | 26.9906 | 27.4906 | 2.4428 |  | 4.4333 |  | 3.9333 |  | 3.4333 |  | 1.9428 |  | 1.4428
1990-08-02 | 28.8 | 30.7368 | 26.4763 | 24.5 | 25 | 25.5 | 26.9763 | 27.4763 | 2.3237 |  | 4.3 |  | 3.8 |  | 3.3 |  | 1.8237 |  | 1.3237
1990-08-03 | 29.475 | 30.6879 | 26.4626 | 24.5 | 25 | 25.5 | 26.9626 | 27.4626 | 3.0124 |  | 4.975 |  | 4.475 |  | 3.975 |  | 2.5124 |  | 2.0124
1990-08-04 | 29.0083 | 30.6143 | 26.442 | 24.5 | 25 | 25.5 | 26.942 | 27.442 | 2.5663 |  | 4.5083 |  | 4.0083 |  | 3.5083 |  | 2.0663 |  | 1.5663
1990-08-05 | 29.8375 | 30.5135 | 26.4138 | 24.5 | 25 | 25.5 | 26.9138 | 27.4138 | 3.4237 |  | 5.3375 |  | 4.8375 |  | 4.3375 |  | 2.9237 |  | 2.4237
1990-08-06 | 29.9333 | 30.4196 | 26.3875 | 24.5 | 25 | 25.5 | 26.8875 | 27.3875 | 3.5458 |  | 5.4333 |  | 4.9333 |  | 4.4333 |  | 3.0458 |  | 2.5458
1990-08-07 | 28.975 | 30.3567 | 26.3699 | 24.5 | 25 | 25.5 | 26.8699 | 27.3699 | 2.6051 |  | 4.475 |  | 3.975 |  | 3.475 |  | 2.1051 |  | 1.6051
1990-08-08 | 29.8542 | 30.3157 | 26.3584 | 24.5 | 25 | 25.5 | 26.8584 | 27.3584 | 3.4958 |  | 5.3542 |  | 4.8542 |  | 4.3542 |  | 2.9958 |  | 2.4958
1990-08-09 | 30.8375 | 30.3031 | 26.3549 | 24.5 | 25 | 25.5 | 26.8549 | 27.3549 | 4.4826 |  | 6.3375 |  | 5.8375 |  | 5.3375 |  | 3.9826 |  | 3.4826
1990-08-10 | 31.575 | 30.2701 | 26.3456 | 24.5 | 25 | 25.5 | 26.8456 | 27.3456 | 5.2294 |  | 7.075 |  | 6.575 |  | 6.075 |  | 4.7294 |  | 4.2294
1990-08-11 | 33.0042 | 30.2689 | 26.3453 | 24.5 | 25 | 25.5 | 26.8453 | 27.3453 | 6.6589 |  | 8.5042 |  | 8.0042 |  | 7.5042 |  | 6.1589 |  | 5.6589
1990-08-12 | 29.3625 | 30.3118 | 26.3573 | 24.5 | 25 | 25.5 | 26.8573 | 27.3573 | 3.0052 |  | 4.8625 |  | 4.3625 |  | 3.8625 |  | 2.5052 |  | 2.0052
1990-08-13 | 29.9292 | 30.281 | 26.3487 | 24.5 | 25 | 25.5 | 26.8487 | 27.3487 | 3.5805 |  | 5.4292 |  | 4.9292 |  | 4.4292 |  | 3.0805 |  | 2.5805
1990-08-14 | 28.5458 | 30.3039 | 26.3551 | 24.5 | 25 | 25.5 | 26.8551 | 27.3551 | 2.1907 |  | 4.0458 |  | 3.5458 |  | 3.0458 |  | 1.6907 |  | 1.1907
1990-08-15 | 28.7542 | 30.3589 | 26.3705 | 24.5 | 25 | 25.5 | 26.8705 | 27.3705 | 2.3837 |  | 4.2542 |  | 3.7542 |  | 3.2542 |  | 1.8837 |  | 1.3837
1990-08-16 | 28.9708 | 30.3164 | 26.3586 | 24.5 | 25 | 25.5 | 26.8586 | 27.3586 | 2.6122 |  | 4.4708 |  | 3.9708 |  | 3.4708 |  | 2.1122 |  | 1.6122
1990-08-17 | 29.05 | 30.2503 | 26.3401 | 24.5 | 25 | 25.5 | 26.8401 | 27.3401 | 2.7099 |  | 4.55 |  | 4.05 |  | 3.55 |  | 2.2099 |  | 1.7099
1990-08-18 | 28.5917 | 30.0857 | 26.294 | 24.5 | 25 | 25.5 | 26.794 | 27.294 | 2.2977 |  | 4.0917 |  | 3.5917 |  | 3.0917 |  | 1.7977 |  | 1.2977
1990-08-19 | 27.8875 | 29.87 | 26.2336 | 24.5 | 25 | 25.5 | 26.7336 | 27.2336 | 1.6539 |  | 3.3875 |  | 2.8875 |  | 2.3875 |  | 1.1539 |  | 0.6539
1990-08-20 | 27.2292 | 29.7017 | 26.1865 | 24.5 | 25 | 25.5 | 26.6865 | 27.1865 | 1.0427 |  | 2.7292 |  | 2.2292 |  | 1.7292 |  | 0.5427 |  | 0.0427
1990-08-21 | 27.9125 | 29.6653 | 26.1763 | 24.5 | 25 | 25.5 | 26.6763 | 27.1763 | 1.7362 |  | 3.4125 |  | 2.9125 |  | 2.4125 |  | 1.2362 |  | 0.73622
1990-08-22 | 28.3542 | 29.5781 | 26.1519 | 24.5 | 25 | 25.5 | 26.6519 | 27.1519 | 2.2023 |  | 3.8542 |  | 3.3542 |  | 2.8542 |  | 1.7023 |  | 1.2023
1990-08-23 | 28.7792 | 29.4733 | 26.1225 | 24.5 | 25 | 25.5 | 26.6225 | 27.1225 | 2.6566 |  | 4.2792 |  | 3.7792 |  | 3.2792 |  | 2.1566 |  | 1.6566
1990-08-24 | 29.1958 | 29.4351 | 26.1118 | 24.5 | 25 | 25.5 | 26.6118 | 27.1118 | 3.084 |  | 4.6958 |  | 4.1958 |  | 3.6958 |  | 2.584 |  | 2.084
1990-08-25 | 29.0625 | 29.404 | 26.1031 | 24.5 | 25 | 25.5 | 26.6031 | 27.1031 | 2.9594 |  | 4.5625 |  | 4.0625 |  | 3.5625 |  | 2.4594 |  | 1.9594
1990-08-26 | 28.7292 | 29.3206 | 26.0798 | 24.5 | 25 | 25.5 | 26.5798 | 27.0798 | 2.6494 |  | 4.2292 |  | 3.7292 |  | 3.2292 |  | 2.1494 |  | 1.6494
1990-08-27 | 29.4042 | 29.2386 | 26.0568 | 24.5 | 25 | 25.5 | 26.5568 | 27.0568 | 3.3474 |  | 4.9042 |  | 4.4042 |  | 3.9042 |  | 2.8474 |  | 2.3474
1990-08-28 | 30.0083 | 29.1979 | 26.0454 | 24.5 | 25 | 25.5 | 26.5454 | 27.0454 | 3.9629 |  | 5.5083 |  | 5.0083 |  | 4.5083 |  | 3.4629 |  | 2.9629
1990-08-29 | 30.5667 | 29.2549 | 26.0614 | 24.5 | 25 | 25.5 | 26.5614 | 27.0614 | 4.5053 |  | 6.0667 |  | 5.5667 |  | 5.0667 |  | 4.0053 |  | 3.5053
1990-08-30 | 31.5667 | 29.3417 | 26.0857 | 24.5 | 25 | 25.5 | 26.5857 | 27.0857 | 5.481 |  | 7.0667 |  | 6.5667 |  | 6.0667 |  | 4.981 |  | 4.481
1990-08-31 | 31.3542 | 29.4044 | 26.1032 | 24.5 | 25 | 25.5 | 26.6032 | 27.1032 | 5.2509 |  | 6.8542 |  | 6.3542 |  | 5.8542 |  | 4.7509 |  | 4.2509
1990-09-01 | 31.7083 | 29.4851 | 26.1258 | 24.5 | 25 | 25.5 | 26.6258 | 27.1258 | 5.5825 |  | 7.2083 |  | 6.7083 |  | 6.2083 |  | 5.0825 |  | 4.5825
1990-09-02 | 31.925 | 29.5821 | 26.153 | 24.5 | 25 | 25.5 | 26.653 | 27.153 | 5.772 |  | 7.425 |  | 6.925 |  | 6.425 |  | 5.272 |  | 4.772
1990-09-03 | 31.1708 | 29.6638 | 26.1759 | 24.5 | 25 | 25.5 | 26.6759 | 27.1759 | 4.995 |  | 6.6708 |  | 6.1708 |  | 5.6708 |  | 4.495 |  | 3.995
1990-09-04 | 30.85 | 29.7358 | 26.196 | 24.5 | 25 | 25.5 | 26.696 | 27.196 | 4.654 |  | 6.35 |  | 5.85 |  | 5.35 |  | 4.154 |  | 3.654
1990-09-05 | 31.4042 | 29.7696 | 26.2055 | 24.5 | 25 | 25.5 | 26.7055 | 27.2055 | 5.1987 |  | 6.9042 |  | 6.4042 |  | 5.9042 |  | 4.6987 |  | 4.1987
1990-09-06 | 32.0292 | 29.8186 | 26.2192 | 24.5 | 25 | 25.5 | 26.7192 | 27.2192 | 5.81 |  | 7.5292 |  | 7.0292 |  | 6.5292 |  | 5.31 |  | 4.81
1990-09-07 | 33.025 | 29.9204 | 26.2477 | 24.5 | 25 | 25.5 | 26.7477 | 27.2477 | 6.7773 |  | 8.525 |  | 8.025 |  | 7.525 |  | 6.2773 |  | 5.7773
1990-09-08 | 32.4792 | 30.0261 | 26.2773 | 24.5 | 25 | 25.5 | 26.7773 | 27.2773 | 6.2019 |  | 7.9792 |  | 7.4792 |  | 6.9792 |  | 5.7019 |  | 5.2019
1990-09-09 | 32.1 | 30.0808 | 26.2926 | 24.5 | 25 | 25.5 | 26.7926 | 27.2926 | 5.8074 |  | 7.6 |  | 7.1 |  | 6.6 |  | 5.3074 |  | 4.8074
1990-09-10 | 32.0625 | 30.0983 | 26.2975 | 24.5 | 25 | 25.5 | 26.7975 | 27.2975 | 5.765 |  | 7.5625 |  | 7.0625 |  | 6.5625 |  | 5.265 |  | 4.765
1990-09-11 | 30.7625 | 30.0669 | 26.2887 | 24.5 | 25 | 25.5 | 26.7887 | 27.2887 | 4.4738 |  | 6.2625 |  | 5.7625 |  | 5.2625 |  | 3.9738 |  | 3.4738
1990-09-12 | 27.8042 | 30.1136 | 26.3018 | 24.5 | 25 | 25.5 | 26.8018 | 27.3018 | 1.5024 |  | 3.3042 |  | 2.8042 |  | 2.3042 |  | 1.0024 |  | 0.50236
1990-09-13 | 27.7542 | 30.0428 | 26.282 | 24.5 | 25 | 25.5 | 26.782 | 27.282 | 1.4722 |  | 3.2542 |  | 2.7542 |  | 2.2542 |  | 0.97219 |  | 0.47219
1990-09-14 | 28.375 | 30.0164 | 26.2746 | 24.5 | 25 | 25.5 | 26.7746 | 27.2746 | 2.1004 |  | 3.875 |  | 3.375 |  | 2.875 |  | 1.6004 |  | 1.1004
1990-09-15 | 26.3083 | 30.0038 | 26.2711 | 24.5 | 25 | 25.5 | 26.7711 | 27.2711 | 0.037283 |  | 1.8083 |  | 1.3083 |  | 0.80833 |  | 0 |  | 0
1990-09-16 | 29.25 | 29.915 | 26.2462 | 24.5 | 25 | 25.5 | 26.7462 | 27.2462 | 3.0038 |  | 4.75 |  | 4.25 |  | 3.75 |  | 2.5038 |  | 2.0038
1990-09-17 | 29.1542 | 29.9217 | 26.2481 | 24.5 | 25 | 25.5 | 26.7481 | 27.2481 | 2.9061 |  | 4.6542 |  | 4.1542 |  | 3.6542 |  | 2.4061 |  | 1.9061
1990-09-18 | 29.275 | 29.9404 | 26.2533 | 24.5 | 25 | 25.5 | 26.7533 | 27.2533 | 3.0217 |  | 4.775 |  | 4.275 |  | 3.775 |  | 2.5217 |  | 2.0217
1990-09-19 | 30.1708 | 29.9867 | 26.2663 | 24.5 | 25 | 25.5 | 26.7663 | 27.2663 | 3.9046 |  | 5.6708 |  | 5.1708 |  | 4.6708 |  | 3.4046 |  | 2.9046
1990-09-20 | 30.2958 | 30.0847 | 26.2937 | 24.5 | 25 | 25.5 | 26.7937 | 27.2937 | 4.0021 |  | 5.7958 |  | 5.2958 |  | 4.7958 |  | 3.5021 |  | 3.0021
1990-09-21 | 31.4292 | 30.1642 | 26.316 | 24.5 | 25 | 25.5 | 26.816 | 27.316 | 5.1132 |  | 6.9292 |  | 6.4292 |  | 5.9292 |  | 4.6132 |  | 4.1132
1990-09-22 | 30.4667 | 30.2667 | 26.3447 | 24.5 | 25 | 25.5 | 26.8447 | 27.3447 | 4.122 |  | 5.9667 |  | 5.4667 |  | 4.9667 |  | 3.622 |  | 3.122
1990-09-23 | 30.2042 | 30.3229 | 26.3604 | 24.5 | 25 | 25.5 | 26.8604 | 27.3604 | 3.8438 |  | 5.7042 |  | 5.2042 |  | 4.7042 |  | 3.3438 |  | 2.8438
1990-09-24 | 28.0375 | 30.3565 | 26.3698 | 24.5 | 25 | 25.5 | 26.8698 | 27.3698 | 1.6677 |  | 3.5375 |  | 3.0375 |  | 2.5375 |  | 1.1677 |  | 0.66767
1990-09-25 | 27.2208 | 30.3224 | 26.3603 | 24.5 | 25 | 25.5 | 26.8603 | 27.3603 | 0.86057 |  | 2.7208 |  | 2.2208 |  | 1.7208 |  | 0.36057 |  | 0
1990-09-26 | 25.6542 | 30.2721 | 26.3462 | 24.5 | 25 | 25.5 | 26.8462 | 27.3462 | 0 |  | 1.1542 |  | 0.65417 |  | 0.15417 |  | 0 |  | 0
1990-09-27 | 25.1667 | 30.1471 | 26.3112 | 24.5 | 25 | 25.5 | 26.8112 | 27.3112 | 0 |  | 0.66667 |  | 0.16667 |  | 0 |  | 0 |  | 0
1990-09-28 | 24.4 | 29.9857 | 26.266 | 24.5 | 25 | 25.5 | 26.766 | 27.266 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-09-29 | 24.475 | 29.7801 | 26.2084 | 24.5 | 25 | 25.5 | 26.7084 | 27.2084 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-09-30 | 24.5333 | 29.5438 | 26.1423 | 24.5 | 25 | 25.5 | 26.6423 | 27.1423 | 0 |  | 0.033333 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-01 | 25.7458 | 29.3164 | 26.0786 | 24.5 | 25 | 25.5 | 26.5786 | 27.0786 | 0 |  | 1.2458 |  | 0.74583 |  | 0.24583 |  | 0 |  | 0
1990-10-02 | 26.0875 | 29.1176 | 26.0229 | 24.5 | 25 | 25.5 | 26.5229 | 27.0229 | 0.064561 |  | 1.5875 |  | 1.0875 |  | 0.5875 |  | 0 |  | 0
1990-10-03 | 27.15 | 28.9231 | 25.9685 | 24.5 | 25 | 25.5 | 26.4685 | 26.9685 | 1.1815 |  | 2.65 |  | 2.15 |  | 1.65 |  | 0.68154 |  | 0.18154
1990-10-04 | 27.6708 | 28.789 | 25.9309 | 24.5 | 25 | 25.5 | 26.4309 | 26.9309 | 1.7399 |  | 3.1708 |  | 2.6708 |  | 2.1708 |  | 1.2399 |  | 0.73991
1990-10-05 | 25.8667 | 28.6831 | 25.9013 | 24.5 | 25 | 25.5 | 26.4013 | 26.9013 | 0 |  | 1.3667 |  | 0.86667 |  | 0.36667 |  | 0 |  | 0
1990-10-06 | 26.5875 | 28.4985 | 25.8496 | 24.5 | 25 | 25.5 | 26.3496 | 26.8496 | 0.73793 |  | 2.0875 |  | 1.5875 |  | 1.0875 |  | 0.23793 |  | 0
1990-10-07 | 27.2417 | 28.3171 | 25.7988 | 24.5 | 25 | 25.5 | 26.2988 | 26.7988 | 1.4429 |  | 2.7417 |  | 2.2417 |  | 1.7417 |  | 0.94288 |  | 0.44288
1990-10-08 | 28.5417 | 28.1243 | 25.7448 | 24.5 | 25 | 25.5 | 26.2448 | 26.7448 | 2.7969 |  | 4.0417 |  | 3.5417 |  | 3.0417 |  | 2.2969 |  | 1.7969
1990-10-09 | 27.5917 | 27.9931 | 25.7081 | 24.5 | 25 | 25.5 | 26.2081 | 26.7081 | 1.8836 |  | 3.0917 |  | 2.5917 |  | 2.0917 |  | 1.3836 |  | 0.88361
1990-10-10 | 28.7333 | 27.8428 | 25.666 | 24.5 | 25 | 25.5 | 26.166 | 26.666 | 3.0674 |  | 4.2333 |  | 3.7333 |  | 3.2333 |  | 2.5674 |  | 2.0674
1990-10-11 | 29.6083 | 27.7318 | 25.6349 | 24.5 | 25 | 25.5 | 26.1349 | 26.6349 | 3.9734 |  | 5.1083 |  | 4.6083 |  | 4.1083 |  | 3.4734 |  | 2.9734
1990-10-12 | 29.2667 | 27.6933 | 25.6241 | 24.5 | 25 | 25.5 | 26.1241 | 26.6241 | 3.6425 |  | 4.7667 |  | 4.2667 |  | 3.7667 |  | 3.1425 |  | 2.6425
1990-10-13 | 29.3167 | 27.7421 | 25.6378 | 24.5 | 25 | 25.5 | 26.1378 | 26.6378 | 3.6789 |  | 4.8167 |  | 4.3167 |  | 3.8167 |  | 3.1789 |  | 2.6789
1990-10-14 | 30.3417 | 27.7942 | 25.6524 | 24.5 | 25 | 25.5 | 26.1524 | 26.6524 | 4.6893 |  | 5.8417 |  | 5.3417 |  | 4.8417 |  | 4.1893 |  | 3.6893
1990-10-15 | 30.5292 | 27.8597 | 25.6707 | 24.5 | 25 | 25.5 | 26.1707 | 26.6707 | 4.8584 |  | 6.0292 |  | 5.5292 |  | 5.0292 |  | 4.3584 |  | 3.8584
1990-10-16 | 29.075 | 28.0004 | 25.7101 | 24.5 | 25 | 25.5 | 26.2101 | 26.7101 | 3.3649 |  | 4.575 |  | 4.075 |  | 3.575 |  | 2.8649 |  | 2.3649
1990-10-17 | 25.6667 | 27.9946 | 25.7085 | 24.5 | 25 | 25.5 | 26.2085 | 26.7085 | 0 |  | 1.1667 |  | 0.66667 |  | 0.16667 |  | 0 |  | 0
1990-10-18 | 25.0833 | 27.8783 | 25.6759 | 24.5 | 25 | 25.5 | 26.1759 | 26.6759 | 0 |  | 0.58333 |  | 0.083333 |  | 0 |  | 0 |  | 0
1990-10-19 | 25.8333 | 27.7386 | 25.6368 | 24.5 | 25 | 25.5 | 26.1368 | 26.6368 | 0.19652 |  | 1.3333 |  | 0.83333 |  | 0.33333 |  | 0 |  | 0
1990-10-20 | 25.1917 | 27.594 | 25.5963 | 24.5 | 25 | 25.5 | 26.0963 | 26.5963 | 0 |  | 0.69167 |  | 0.19167 |  | 0 |  | 0 |  | 0
1990-10-21 | 23.8917 | 27.4239 | 25.5487 | 24.5 | 25 | 25.5 | 26.0487 | 26.5487 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-22 | 22.3583 | 27.1726 | 25.4783 | 24.5 | 25 | 25.5 | 25.9783 | 26.4783 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-23 | 21.975 | 26.9024 | 25.4027 | 24.5 | 25 | 25.5 | 25.9027 | 26.4027 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-24 | 21.9208 | 26.6281 | 25.3259 | 24.5 | 25 | 25.5 | 25.8259 | 26.3259 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-25 | 22.05 | 26.4242 | 25.2688 | 24.5 | 25 | 25.5 | 25.7688 | 26.2688 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-26 | 17.5792 | 26.2518 | 25.2205 | 24.5 | 25 | 25.5 | 25.7205 | 26.2205 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-27 | 21.0333 | 25.9826 | 25.1451 | 24.5 | 25 | 25.5 | 25.6451 | 26.1451 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-28 | 21.7292 | 25.8449 | 25.1066 | 24.5 | 25 | 25.5 | 25.6066 | 26.1066 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-29 | 21.35 | 25.7558 | 25.0816 | 24.5 | 25 | 25.5 | 25.5816 | 26.0816 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-30 | 21.2417 | 25.6517 | 25.0525 | 24.5 | 25 | 25.5 | 25.5525 | 26.0525 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-31 | 21.0708 | 25.5419 | 25.0217 | 24.5 | 25 | 25.5 | 25.5217 | 26.0217 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-01 | 22.8125 | 25.3861 | 24.9781 | 24.5 | 25 | 25.5 | 25.4781 | 25.9781 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-02 | 22.7 | 25.2769 | 24.9475 | 24.5 | 25 | 25.5 | 25.4475 | 25.9475 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-03 | 23.6167 | 25.1286 | 24.906 | 24.5 | 25 | 25.5 | 25.406 | 25.906 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-04 | 24.175 | 24.9935 | 24.8682 | 24.5 | 25 | 25.5 | 25.3682 | 25.8682 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-05 | 23.6667 | 24.9371 | 24.8524 | 24.5 | 25 | 25.5 | 25.3524 | 25.8524 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-06 | 24.8833 | 24.8397 | 24.8251 | 24.5 | 25 | 25.5 | 25.3251 | 25.8251 | 0.058211 |  | 0.38333 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-07 | 24.2958 | 24.7611 | 24.8031 | 24.5 | 25 | 25.5 | 25.3031 | 25.8031 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-08 | 21.6292 | 24.6196 | 24.7635 | 24.5 | 25 | 25.5 | 25.2635 | 25.7635 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-09 | 20.75 | 24.4208 | 24.7078 | 24.5 | 25 | 25.5 | 25.2078 | 25.7078 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-10 | 21.225 | 24.1547 | 24.6333 | 24.5 | 25 | 25.5 | 25.1333 | 25.6333 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-11 | 20.2458 | 23.8753 | 24.5551 | 24.5 | 25 | 25.5 | 25.0551 | 25.5551 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-12 | 20.85 | 23.5746 | 24.4709 | 24.5 | 25 | 25.5 | 24.9709 | 25.4709 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-13 | 21.7792 | 23.2924 | 24.3919 | 24.5 | 25 | 25.5 | 24.8919 | 25.3919 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-14 | 23.8167 | 23.0069 | 24.3119 | 24.5 | 25 | 25.5 | 24.8119 | 25.3119 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-15 | 20.1667 | 22.7832 | 24.2493 | 24.5 | 25 | 25.5 | 24.7493 | 25.2493 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-16 | 19.475 | 22.4863 | 24.1662 | 24.5 | 25 | 25.5 | 24.6662 | 25.1662 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-17 | 18.9958 | 22.2799 | 24.1084 | 24.5 | 25 | 25.5 | 24.6084 | 25.1084 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-18 | 18.725 | 22.0769 | 24.0515 | 24.5 | 25 | 25.5 | 24.5515 | 25.0515 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-19 | 18.8 | 21.84 | 23.9852 | 24.5 | 25 | 25.5 | 24.4852 | 24.9852 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-20 | 19.2375 | 21.6269 | 23.9255 | 24.5 | 25 | 25.5 | 24.4255 | 24.9255 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-21 | 18.8708 | 21.4718 | 23.8821 | 24.5 | 25 | 25.5 | 24.3821 | 24.8821 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-22 | 18.7125 | 21.3556 | 23.8496 | 24.5 | 25 | 25.5 | 24.3496 | 24.8496 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-23 | 18.4583 | 21.2468 | 23.8191 | 24.5 | 25 | 25.5 | 24.3191 | 24.8191 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-24 | 18.2458 | 21.1314 | 23.7868 | 24.5 | 25 | 25.5 | 24.2868 | 24.7868 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-25 | 18.7792 | 21.0046 | 23.7513 | 24.5 | 25 | 25.5 | 24.2513 | 24.7513 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-26 | 19.925 | 21.0446 | 23.7625 | 24.5 | 25 | 25.5 | 24.2625 | 24.7625 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-27 | 19.8333 | 21.0076 | 23.7521 | 24.5 | 25 | 25.5 | 24.2521 | 24.7521 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-28 | 18.0542 | 20.9444 | 23.7344 | 24.5 | 25 | 25.5 | 24.2344 | 24.7344 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-29 | 17.3333 | 20.8346 | 23.7037 | 24.5 | 25 | 25.5 | 24.2037 | 24.7037 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-30 | 16.9917 | 20.7043 | 23.6672 | 24.5 | 25 | 25.5 | 24.1672 | 24.6672 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-01 | 16.8292 | 20.5683 | 23.6291 | 24.5 | 25 | 25.5 | 24.1291 | 24.6291 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-02 | 16.1333 | 20.3689 | 23.5733 | 24.5 | 25 | 25.5 | 24.0733 | 24.5733 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-03 | 16.075 | 20.15 | 23.512 | 24.5 | 25 | 25.5 | 24.012 | 24.512 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-04 | 15.925 | 19.8986 | 23.4416 | 24.5 | 25 | 25.5 | 23.9416 | 24.4416 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-05 | 15.9125 | 19.6236 | 23.3646 | 24.5 | 25 | 25.5 | 23.8646 | 24.3646 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-06 | 16 | 19.3651 | 23.2922 | 24.5 | 25 | 25.5 | 23.7922 | 24.2922 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-07 | 16.1125 | 19.069 | 23.2093 | 24.5 | 25 | 25.5 | 23.7093 | 24.2093 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-08 | 16.4167 | 18.7962 | 23.133 | 24.5 | 25 | 25.5 | 23.633 | 24.133 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-09 | 16.4542 | 18.6225 | 23.0843 | 24.5 | 25 | 25.5 | 23.5843 | 24.0843 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-10 | 16.325 | 18.4793 | 23.0442 | 24.5 | 25 | 25.5 | 23.5442 | 24.0442 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-11 | 16.5333 | 18.316 | 22.9985 | 24.5 | 25 | 25.5 | 23.4985 | 23.9985 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-12 | 18.3458 | 18.1922 | 22.9638 | 24.5 | 25 | 25.5 | 23.4638 | 23.9638 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-13 | 19.9875 | 18.1088 | 22.9405 | 24.5 | 25 | 25.5 | 23.4405 | 23.9405 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-14 | 14.4208 | 18.049 | 22.9237 | 24.5 | 25 | 25.5 | 23.4237 | 23.9237 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-15 | 12.625 | 17.7358 | 22.836 | 24.5 | 25 | 25.5 | 23.336 | 23.836 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-16 | 11.3875 | 17.4844 | 22.7656 | 24.5 | 25 | 25.5 | 23.2656 | 23.7656 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-17 | 13.3792 | 17.2149 | 22.6902 | 24.5 | 25 | 25.5 | 23.1902 | 23.6902 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-18 | 15.0083 | 17.0276 | 22.6377 | 24.5 | 25 | 25.5 | 23.1377 | 23.6377 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-19 | 13.6625 | 16.9037 | 22.6031 | 24.5 | 25 | 25.5 | 23.1031 | 23.6031 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-20 | 11.7292 | 16.7325 | 22.5551 | 24.5 | 25 | 25.5 | 23.0551 | 23.5551 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-21 | 11.6417 | 16.4822 | 22.485 | 24.5 | 25 | 25.5 | 22.985 | 23.485 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-22 | 12.2625 | 16.2413 | 22.4176 | 24.5 | 25 | 25.5 | 22.9176 | 23.4176 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-23 | 11.5958 | 16.0263 | 22.3574 | 24.5 | 25 | 25.5 | 22.8574 | 23.3574 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-24 | 12.0125 | 15.7975 | 22.2933 | 24.5 | 25 | 25.5 | 22.7933 | 23.2933 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-25 | 11.9208 | 15.5897 | 22.2351 | 24.5 | 25 | 25.5 | 22.7351 | 23.2351 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-26 | 13.3792 | 15.3611 | 22.1711 | 24.5 | 25 | 25.5 | 22.6711 | 23.1711 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-27 | 13.1833 | 15.1429 | 22.11 | 24.5 | 25 | 25.5 | 22.61 | 23.11 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-28 | 12.9042 | 14.9213 | 22.048 | 24.5 | 25 | 25.5 | 22.548 | 23.048 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-29 | 13.2583 | 14.7496 | 21.9999 | 24.5 | 25 | 25.5 | 22.4999 | 22.9999 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-30 | 12.9958 | 14.6138 | 21.9619 | 24.5 | 25 | 25.5 | 22.4619 | 22.9619 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-31 | 11.9 | 14.4806 | 21.9246 | 24.5 | 25 | 25.5 | 22.4246 | 22.9246 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## Pilani
Date | Daywise mean temperature | Running mean temperature (RMT) | Neutral temperature_IMAC | Baseline temperature calculated from PMV model | Plant adjusted I (Baseline + 0.5°C) | Plant adjusted II (Baseline + 1°C) | Plant adjusted I+ IMAC | Plant adjusted II+ IMAC | ACDD based on IMAC neutral temperature | 875.6863 | ACDD based on baseline temperature i.e. 24.5 calculated from the PMV model | 1228.2792 | ACDD based on 0.5°C adjustment on baseline temperature because of plant | 1118.45 | ACDD based on 1°C adjustment on baseline temperature because of plant | 1010.3833 | ACDD based on IMAC neutral temperature considering 0.5°C plant effect | 774.2798 | ACDD based on IMAC neutral temperature considering 1°C plant effect | 678.2748
2021-01-01 | 11.0542 | 13.9203 | 21.7677 | 24.5 | 25 | 25.5 | 22.2677 | 22.7677 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-02 | 12.0208 | 13.7882 | 21.7307 | 24.5 | 25 | 25.5 | 22.2307 | 22.7307 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-03 | 13.1417 | 13.6699 | 21.6976 | 24.5 | 25 | 25.5 | 22.1976 | 22.6976 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-04 | 14.7375 | 13.5458 | 21.6628 | 24.5 | 25 | 25.5 | 22.1628 | 22.6628 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-05 | 13.2417 | 13.449 | 21.6357 | 24.5 | 25 | 25.5 | 22.1357 | 22.6357 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-06 | 14.6375 | 13.3024 | 21.5947 | 24.5 | 25 | 25.5 | 22.0947 | 22.5947 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-07 | 16.0292 | 13.2764 | 21.5874 | 24.5 | 25 | 25.5 | 22.0874 | 22.5874 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-08 | 15.3667 | 13.3236 | 21.6006 | 24.5 | 25 | 25.5 | 22.1006 | 22.6006 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-09 | 10.9292 | 13.3583 | 21.6103 | 24.5 | 25 | 25.5 | 22.1103 | 22.6103 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-10 | 10.6583 | 13.2596 | 21.5827 | 24.5 | 25 | 25.5 | 22.0827 | 22.5827 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-11 | 8.8875 | 13.171 | 21.5579 | 24.5 | 25 | 25.5 | 22.0579 | 22.5579 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-12 | 11.0708 | 12.9975 | 21.5093 | 24.5 | 25 | 25.5 | 22.0093 | 22.5093 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-13 | 10.8625 | 12.9132 | 21.4857 | 24.5 | 25 | 25.5 | 21.9857 | 22.4857 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-14 | 10.4167 | 12.8119 | 21.4573 | 24.5 | 25 | 25.5 | 21.9573 | 22.4573 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-15 | 8.4208 | 12.7471 | 21.4392 | 24.5 | 25 | 25.5 | 21.9392 | 22.4392 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-16 | 9.4375 | 12.6369 | 21.4083 | 24.5 | 25 | 25.5 | 21.9083 | 22.4083 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-17 | 8.6292 | 12.6276 | 21.4057 | 24.5 | 25 | 25.5 | 21.9057 | 22.4057 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-18 | 10.5125 | 12.6099 | 21.4008 | 24.5 | 25 | 25.5 | 21.9008 | 22.4008 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-19 | 11.4042 | 12.6467 | 21.4111 | 24.5 | 25 | 25.5 | 21.9111 | 22.4111 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-20 | 12.4708 | 12.6253 | 21.4051 | 24.5 | 25 | 25.5 | 21.9051 | 22.4051 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-21 | 12.1958 | 12.5792 | 21.3922 | 24.5 | 25 | 25.5 | 21.8922 | 22.3922 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-22 | 12.7167 | 12.4906 | 21.3674 | 24.5 | 25 | 25.5 | 21.8674 | 22.3674 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-23 | 12.3125 | 12.3921 | 21.3398 | 24.5 | 25 | 25.5 | 21.8398 | 22.3398 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-24 | 11.2208 | 12.2567 | 21.3019 | 24.5 | 25 | 25.5 | 21.8019 | 22.3019 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-25 | 10.0667 | 12.0913 | 21.2556 | 24.5 | 25 | 25.5 | 21.7556 | 22.2556 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-26 | 10.9833 | 11.8903 | 21.1993 | 24.5 | 25 | 25.5 | 21.6993 | 22.1993 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-27 | 11.4417 | 11.7444 | 21.1584 | 24.5 | 25 | 25.5 | 21.6584 | 22.1584 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-28 | 12.2208 | 11.6453 | 21.1307 | 24.5 | 25 | 25.5 | 21.6307 | 22.1307 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-29 | 14.0167 | 11.6542 | 21.1332 | 24.5 | 25 | 25.5 | 21.6332 | 22.1332 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-30 | 14.2542 | 11.7436 | 21.1582 | 24.5 | 25 | 25.5 | 21.6582 | 22.1582 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-01-31 | 15.7167 | 11.8453 | 21.1867 | 24.5 | 25 | 25.5 | 21.6867 | 22.1867 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-01 | 14.0417 | 12.0007 | 21.2302 | 24.5 | 25 | 25.5 | 21.7302 | 22.2302 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-02 | 15.1583 | 12.0681 | 21.2491 | 24.5 | 25 | 25.5 | 21.7491 | 22.2491 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-03 | 13.1208 | 12.1353 | 21.2679 | 24.5 | 25 | 25.5 | 21.7679 | 22.2679 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-04 | 11.9417 | 12.0814 | 21.2528 | 24.5 | 25 | 25.5 | 21.7528 | 22.2528 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-05 | 12.175 | 12.0381 | 21.2407 | 24.5 | 25 | 25.5 | 21.7407 | 22.2407 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-06 | 15.6583 | 11.956 | 21.2177 | 24.5 | 25 | 25.5 | 21.7177 | 22.2177 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-07 | 17.7792 | 11.9436 | 21.2142 | 24.5 | 25 | 25.5 | 21.7142 | 22.2142 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-08 | 16.9667 | 12.024 | 21.2367 | 24.5 | 25 | 25.5 | 21.7367 | 22.2367 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-09 | 16.2417 | 12.2253 | 21.2931 | 24.5 | 25 | 25.5 | 21.7931 | 22.2931 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-10 | 15.2083 | 12.4114 | 21.3452 | 24.5 | 25 | 25.5 | 21.8452 | 22.3452 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-11 | 14.85 | 12.6221 | 21.4042 | 24.5 | 25 | 25.5 | 21.9042 | 22.4042 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-12 | 15.3625 | 12.7481 | 21.4395 | 24.5 | 25 | 25.5 | 21.9395 | 22.4395 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-13 | 17.05 | 12.8981 | 21.4815 | 24.5 | 25 | 25.5 | 21.9815 | 22.4815 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-14 | 17.8708 | 13.1192 | 21.5434 | 24.5 | 25 | 25.5 | 22.0434 | 22.5434 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-15 | 17.8833 | 13.4342 | 21.6316 | 24.5 | 25 | 25.5 | 22.1316 | 22.6316 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-16 | 17.5792 | 13.7157 | 21.7104 | 24.5 | 25 | 25.5 | 22.2104 | 22.7104 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-17 | 18.3208 | 14.014 | 21.7939 | 24.5 | 25 | 25.5 | 22.2939 | 22.7939 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-18 | 17.8917 | 14.2743 | 21.8668 | 24.5 | 25 | 25.5 | 22.3668 | 22.8668 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-19 | 17.7708 | 14.4906 | 21.9274 | 24.5 | 25 | 25.5 | 22.4274 | 22.9274 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-20 | 17.7 | 14.6672 | 21.9768 | 24.5 | 25 | 25.5 | 22.4768 | 22.9768 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-21 | 18.6667 | 14.8507 | 22.0282 | 24.5 | 25 | 25.5 | 22.5282 | 23.0282 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-22 | 22.1208 | 15.049 | 22.0837 | 24.5 | 25 | 25.5 | 22.5837 | 23.0837 | 0.037106 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-23 | 20.1583 | 15.376 | 22.1753 | 24.5 | 25 | 25.5 | 22.6753 | 23.1753 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-24 | 19.825 | 15.6739 | 22.2587 | 24.5 | 25 | 25.5 | 22.7587 | 23.2587 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-25 | 20.0875 | 15.9992 | 22.3498 | 24.5 | 25 | 25.5 | 22.8498 | 23.3498 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-26 | 18.3583 | 16.3026 | 22.4347 | 24.5 | 25 | 25.5 | 22.9347 | 23.4347 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-27 | 17.675 | 16.5332 | 22.4993 | 24.5 | 25 | 25.5 | 22.9993 | 23.4993 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-02-28 | 17.075 | 16.715 | 22.5502 | 24.5 | 25 | 25.5 | 23.0502 | 23.5502 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-01 | 18.2542 | 16.8169 | 22.5787 | 24.5 | 25 | 25.5 | 23.0787 | 23.5787 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-02 | 19.8125 | 16.9503 | 22.6161 | 24.5 | 25 | 25.5 | 23.1161 | 23.6161 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-03 | 20.2083 | 17.0868 | 22.6543 | 24.5 | 25 | 25.5 | 23.1543 | 23.6543 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-04 | 18.7333 | 17.2924 | 22.7119 | 24.5 | 25 | 25.5 | 23.2119 | 23.7119 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-05 | 19.0833 | 17.4115 | 22.7452 | 24.5 | 25 | 25.5 | 23.2452 | 23.7452 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-06 | 20.6083 | 17.6103 | 22.8009 | 24.5 | 25 | 25.5 | 23.3009 | 23.8009 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-07 | 23.2208 | 17.8992 | 22.8818 | 24.5 | 25 | 25.5 | 23.3818 | 23.8818 | 0.33907 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-08 | 23 | 18.2674 | 22.9849 | 24.5 | 25 | 25.5 | 23.4849 | 23.9849 | 0.015139 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-09 | 22.6583 | 18.5121 | 23.0534 | 24.5 | 25 | 25.5 | 23.5534 | 24.0534 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-10 | 22.7458 | 18.6747 | 23.0989 | 24.5 | 25 | 25.5 | 23.5989 | 24.0989 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-11 | 23.2458 | 18.8674 | 23.1529 | 24.5 | 25 | 25.5 | 23.6529 | 24.1529 | 0.092972 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-12 | 23.2917 | 19.1008 | 23.2182 | 24.5 | 25 | 25.5 | 23.7182 | 24.2182 | 0.073433 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-03-13 | 25.7708 | 19.3703 | 23.2937 | 24.5 | 25 | 25.5 | 23.7937 | 24.2937 | 2.4772 |  | 1.2708 |  | 0.77083 |  | 0.27083 |  | 1.9772 |  | 1.4772
2021-03-14 | 26.9875 | 19.7343 | 23.3956 | 24.5 | 25 | 25.5 | 23.8956 | 24.3956 | 3.5919 |  | 2.4875 |  | 1.9875 |  | 1.4875 |  | 3.0919 |  | 2.5919
2021-03-15 | 28.375 | 20.1218 | 23.5041 | 24.5 | 25 | 25.5 | 24.0041 | 24.5041 | 4.8709 |  | 3.875 |  | 3.375 |  | 2.875 |  | 4.3709 |  | 3.8709
2021-03-16 | 28.1292 | 20.4993 | 23.6098 | 24.5 | 25 | 25.5 | 24.1098 | 24.6098 | 4.5194 |  | 3.6292 |  | 3.1292 |  | 2.6292 |  | 4.0194 |  | 3.5194
2021-03-17 | 28.4417 | 20.8412 | 23.7055 | 24.5 | 25 | 25.5 | 24.2055 | 24.7055 | 4.7361 |  | 3.9417 |  | 3.4417 |  | 2.9417 |  | 4.2361 |  | 3.7361
2021-03-18 | 29.6667 | 21.1932 | 23.8041 | 24.5 | 25 | 25.5 | 24.3041 | 24.8041 | 5.8626 |  | 5.1667 |  | 4.6667 |  | 4.1667 |  | 5.3626 |  | 4.8626
2021-03-19 | 29.7125 | 21.5961 | 23.9169 | 24.5 | 25 | 25.5 | 24.4169 | 24.9169 | 5.7956 |  | 5.2125 |  | 4.7125 |  | 4.2125 |  | 5.2956 |  | 4.7956
2021-03-20 | 29.5917 | 21.9758 | 24.0232 | 24.5 | 25 | 25.5 | 24.5232 | 25.0232 | 5.5684 |  | 5.0917 |  | 4.5917 |  | 4.0917 |  | 5.0684 |  | 4.5684
2021-03-21 | 29.3 | 22.3658 | 24.1324 | 24.5 | 25 | 25.5 | 24.6324 | 25.1324 | 5.1676 |  | 4.8 |  | 4.3 |  | 3.8 |  | 4.6676 |  | 4.1676
2021-03-22 | 28.3958 | 22.7501 | 24.24 | 24.5 | 25 | 25.5 | 24.74 | 25.24 | 4.1558 |  | 3.8958 |  | 3.3958 |  | 2.8958 |  | 3.6558 |  | 3.1558
2021-03-23 | 28.375 | 23.1067 | 24.3399 | 24.5 | 25 | 25.5 | 24.8399 | 25.3399 | 4.0351 |  | 3.875 |  | 3.375 |  | 2.875 |  | 3.5351 |  | 3.0351
2021-03-24 | 28.5667 | 23.4303 | 24.4305 | 24.5 | 25 | 25.5 | 24.9305 | 25.4305 | 4.1362 |  | 4.0667 |  | 3.5667 |  | 3.0667 |  | 3.6362 |  | 3.1362
2021-03-25 | 28.0125 | 23.6451 | 24.4906 | 24.5 | 25 | 25.5 | 24.9906 | 25.4906 | 3.5219 |  | 3.5125 |  | 3.0125 |  | 2.5125 |  | 3.0219 |  | 2.5219
2021-03-26 | 27.8625 | 23.9069 | 24.5639 | 24.5 | 25 | 25.5 | 25.0639 | 25.5639 | 3.2986 |  | 3.3625 |  | 2.8625 |  | 2.3625 |  | 2.7986 |  | 2.2986
2021-03-27 | 28.8667 | 24.1749 | 24.639 | 24.5 | 25 | 25.5 | 25.139 | 25.639 | 4.2277 |  | 4.3667 |  | 3.8667 |  | 3.3667 |  | 3.7277 |  | 3.2277
2021-03-28 | 30.3458 | 24.4675 | 24.7209 | 24.5 | 25 | 25.5 | 25.2209 | 25.7209 | 5.6249 |  | 5.8458 |  | 5.3458 |  | 4.8458 |  | 5.1249 |  | 4.6249
2021-03-29 | 31.2583 | 24.8671 | 24.8328 | 24.5 | 25 | 25.5 | 25.3328 | 25.8328 | 6.4255 |  | 6.7583 |  | 6.2583 |  | 5.7583 |  | 5.9255 |  | 5.4255
2021-03-30 | 31.4042 | 25.3199 | 24.9596 | 24.5 | 25 | 25.5 | 25.4596 | 25.9596 | 6.4446 |  | 6.9042 |  | 6.4042 |  | 5.9042 |  | 5.9446 |  | 5.4446
2021-03-31 | 30.8208 | 25.7975 | 25.0933 | 24.5 | 25 | 25.5 | 25.5933 | 26.0933 | 5.7275 |  | 6.3208 |  | 5.8208 |  | 5.3208 |  | 5.2275 |  | 4.7275
2021-04-01 | 26.2208 | 26.2164 | 25.2106 | 24.5 | 25 | 25.5 | 25.7106 | 26.2106 | 1.0102 |  | 1.7208 |  | 1.2208 |  | 0.72083 |  | 0.51024 |  | 0.010244
2021-04-02 | 25.575 | 26.43 | 25.2704 | 24.5 | 25 | 25.5 | 25.7704 | 26.2704 | 0.3046 |  | 1.075 |  | 0.575 |  | 0.075 |  | 0 |  | 0
2021-04-03 | 26.8417 | 26.6089 | 25.3205 | 24.5 | 25 | 25.5 | 25.8205 | 26.3205 | 1.5212 |  | 2.3417 |  | 1.8417 |  | 1.3417 |  | 1.0212 |  | 0.52118
2021-04-04 | 28.0208 | 26.8792 | 25.3962 | 24.5 | 25 | 25.5 | 25.8962 | 26.3962 | 2.6247 |  | 3.5208 |  | 3.0208 |  | 2.5208 |  | 2.1247 |  | 1.6247
2021-04-05 | 30.6292 | 27.1771 | 25.4796 | 24.5 | 25 | 25.5 | 25.9796 | 26.4796 | 5.1496 |  | 6.1292 |  | 5.6292 |  | 5.1292 |  | 4.6496 |  | 4.1496
2021-04-06 | 30.5667 | 27.5111 | 25.5731 | 24.5 | 25 | 25.5 | 26.0731 | 26.5731 | 4.9936 |  | 6.0667 |  | 5.5667 |  | 5.0667 |  | 4.4936 |  | 3.9936
2021-04-07 | 27.6083 | 27.756 | 25.6417 | 24.5 | 25 | 25.5 | 26.1417 | 26.6417 | 1.9667 |  | 3.1083 |  | 2.6083 |  | 2.1083 |  | 1.4667 |  | 0.96666
2021-04-08 | 26.5458 | 27.9096 | 25.6847 | 24.5 | 25 | 25.5 | 26.1847 | 26.6847 | 0.86115 |  | 2.0458 |  | 1.5458 |  | 1.0458 |  | 0.36115 |  | 0
2021-04-09 | 27.6625 | 28.0392 | 25.721 | 24.5 | 25 | 25.5 | 26.221 | 26.721 | 1.9415 |  | 3.1625 |  | 2.6625 |  | 2.1625 |  | 1.4415 |  | 0.94153
2021-04-10 | 28.675 | 28.2031 | 25.7669 | 24.5 | 25 | 25.5 | 26.2669 | 26.7669 | 2.9081 |  | 4.175 |  | 3.675 |  | 3.175 |  | 2.4081 |  | 1.9081
2021-04-11 | 29.825 | 28.384 | 25.8175 | 24.5 | 25 | 25.5 | 26.3175 | 26.8175 | 4.0075 |  | 5.325 |  | 4.825 |  | 4.325 |  | 3.5075 |  | 3.0075
2021-04-12 | 30.8125 | 28.6018 | 25.8785 | 24.5 | 25 | 25.5 | 26.3785 | 26.8785 | 4.934 |  | 6.3125 |  | 5.8125 |  | 5.3125 |  | 4.434 |  | 3.934
2021-04-13 | 31.6167 | 28.7699 | 25.9256 | 24.5 | 25 | 25.5 | 26.4256 | 26.9256 | 5.6911 |  | 7.1167 |  | 6.6167 |  | 6.1167 |  | 5.1911 |  | 4.6911
2021-04-14 | 30.1417 | 28.9242 | 25.9688 | 24.5 | 25 | 25.5 | 26.4688 | 26.9688 | 4.1729 |  | 5.6417 |  | 5.1417 |  | 4.6417 |  | 3.6729 |  | 3.1729
2021-04-15 | 31.1083 | 28.9831 | 25.9853 | 24.5 | 25 | 25.5 | 26.4853 | 26.9853 | 5.1231 |  | 6.6083 |  | 6.1083 |  | 5.6083 |  | 4.6231 |  | 4.1231
2021-04-16 | 25.7833 | 29.0824 | 26.0131 | 24.5 | 25 | 25.5 | 26.5131 | 27.0131 | 0 |  | 1.2833 |  | 0.78333 |  | 0.28333 |  | 0 |  | 0
2021-04-17 | 25.0583 | 28.9938 | 25.9883 | 24.5 | 25 | 25.5 | 26.4883 | 26.9883 | 0 |  | 0.55833 |  | 0.058333 |  | 0 |  | 0 |  | 0
2021-04-18 | 27.7792 | 28.8401 | 25.9452 | 24.5 | 25 | 25.5 | 26.4452 | 26.9452 | 1.8339 |  | 3.2792 |  | 2.7792 |  | 2.2792 |  | 1.3339 |  | 0.83393
2021-04-19 | 29.85 | 28.7757 | 25.9272 | 24.5 | 25 | 25.5 | 26.4272 | 26.9272 | 3.9228 |  | 5.35 |  | 4.85 |  | 4.35 |  | 3.4228 |  | 2.9228
2021-04-20 | 26.5958 | 28.7843 | 25.9296 | 24.5 | 25 | 25.5 | 26.4296 | 26.9296 | 0.66623 |  | 2.0958 |  | 1.5958 |  | 1.0958 |  | 0.16623 |  | 0
2021-04-21 | 23.5208 | 28.6942 | 25.9044 | 24.5 | 25 | 25.5 | 26.4044 | 26.9044 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-04-22 | 27.3583 | 28.5317 | 25.8589 | 24.5 | 25 | 25.5 | 26.3589 | 26.8589 | 1.4995 |  | 2.8583 |  | 2.3583 |  | 1.8583 |  | 0.99947 |  | 0.49947
2021-04-23 | 27.9083 | 28.4978 | 25.8494 | 24.5 | 25 | 25.5 | 26.3494 | 26.8494 | 2.059 |  | 3.4083 |  | 2.9083 |  | 2.4083 |  | 1.559 |  | 1.059
2021-04-24 | 26.15 | 28.4758 | 25.8432 | 24.5 | 25 | 25.5 | 26.3432 | 26.8432 | 0.30677 |  | 1.65 |  | 1.15 |  | 0.65 |  | 0 |  | 0
2021-04-25 | 28.1417 | 28.4137 | 25.8259 | 24.5 | 25 | 25.5 | 26.3259 | 26.8259 | 2.3158 |  | 3.6417 |  | 3.1417 |  | 2.6417 |  | 1.8158 |  | 1.3158
2021-04-26 | 30.5875 | 28.4231 | 25.8285 | 24.5 | 25 | 25.5 | 26.3285 | 26.8285 | 4.759 |  | 6.0875 |  | 5.5875 |  | 5.0875 |  | 4.259 |  | 3.759
2021-04-27 | 32.7833 | 28.4804 | 25.8445 | 24.5 | 25 | 25.5 | 26.3445 | 26.8445 | 6.9388 |  | 8.2833 |  | 7.7833 |  | 7.2833 |  | 6.4388 |  | 5.9388
2021-04-28 | 33.6583 | 28.5617 | 25.8673 | 24.5 | 25 | 25.5 | 26.3673 | 26.8673 | 7.7911 |  | 9.1583 |  | 8.6583 |  | 8.1583 |  | 7.2911 |  | 6.7911
2021-04-29 | 33.95 | 28.6417 | 25.8897 | 24.5 | 25 | 25.5 | 26.3897 | 26.8897 | 8.0603 |  | 9.45 |  | 8.95 |  | 8.45 |  | 7.5603 |  | 7.0603
2021-04-30 | 34.7917 | 28.7265 | 25.9134 | 24.5 | 25 | 25.5 | 26.4134 | 26.9134 | 8.8782 |  | 10.2917 |  | 9.7917 |  | 9.2917 |  | 8.3782 |  | 7.8782
2021-05-01 | 32.6458 | 28.8589 | 25.9505 | 24.5 | 25 | 25.5 | 26.4505 | 26.9505 | 6.6953 |  | 8.1458 |  | 7.6458 |  | 7.1458 |  | 6.1953 |  | 5.6953
2021-05-02 | 31.1583 | 29.0731 | 26.0105 | 24.5 | 25 | 25.5 | 26.5105 | 27.0105 | 5.1479 |  | 6.6583 |  | 6.1583 |  | 5.6583 |  | 4.6479 |  | 4.1479
2021-05-03 | 31.8792 | 29.2592 | 26.0626 | 24.5 | 25 | 25.5 | 26.5626 | 27.0626 | 5.8166 |  | 7.3792 |  | 6.8792 |  | 6.3792 |  | 5.3166 |  | 4.8166
2021-05-04 | 32.6417 | 29.4271 | 26.1096 | 24.5 | 25 | 25.5 | 26.6096 | 27.1096 | 6.5321 |  | 8.1417 |  | 7.6417 |  | 7.1417 |  | 6.0321 |  | 5.5321
2021-05-05 | 32.8792 | 29.5811 | 26.1527 | 24.5 | 25 | 25.5 | 26.6527 | 27.1527 | 6.7265 |  | 8.3792 |  | 7.8792 |  | 7.3792 |  | 6.2265 |  | 5.7265
2021-05-06 | 29.4625 | 29.6561 | 26.1737 | 24.5 | 25 | 25.5 | 26.6737 | 27.1737 | 3.2888 |  | 4.9625 |  | 4.4625 |  | 3.9625 |  | 2.7888 |  | 2.2888
2021-05-07 | 28.6125 | 29.6193 | 26.1634 | 24.5 | 25 | 25.5 | 26.6634 | 27.1634 | 2.4491 |  | 4.1125 |  | 3.6125 |  | 3.1125 |  | 1.9491 |  | 1.4491
2021-05-08 | 31.6208 | 29.6528 | 26.1728 | 24.5 | 25 | 25.5 | 26.6728 | 27.1728 | 5.4481 |  | 7.1208 |  | 6.6208 |  | 6.1208 |  | 4.9481 |  | 4.4481
2021-05-09 | 33.0667 | 29.8219 | 26.2201 | 24.5 | 25 | 25.5 | 26.7201 | 27.2201 | 6.8465 |  | 8.5667 |  | 8.0667 |  | 7.5667 |  | 6.3465 |  | 5.8465
2021-05-10 | 30.7625 | 30.0021 | 26.2706 | 24.5 | 25 | 25.5 | 26.7706 | 27.2706 | 4.4919 |  | 6.2625 |  | 5.7625 |  | 5.2625 |  | 3.9919 |  | 3.4919
2021-05-11 | 31.5083 | 30.0717 | 26.2901 | 24.5 | 25 | 25.5 | 26.7901 | 27.2901 | 5.2183 |  | 7.0083 |  | 6.5083 |  | 6.0083 |  | 4.7183 |  | 4.2183
2021-05-12 | 30.1542 | 30.1278 | 26.3058 | 24.5 | 25 | 25.5 | 26.8058 | 27.3058 | 3.8484 |  | 5.6542 |  | 5.1542 |  | 4.6542 |  | 3.3484 |  | 2.8484
2021-05-13 | 29.7917 | 30.1058 | 26.2996 | 24.5 | 25 | 25.5 | 26.7996 | 27.2996 | 3.492 |  | 5.2917 |  | 4.7917 |  | 4.2917 |  | 2.992 |  | 2.492
2021-05-14 | 31.6 | 30.045 | 26.2826 | 24.5 | 25 | 25.5 | 26.7826 | 27.2826 | 5.3174 |  | 7.1 |  | 6.6 |  | 6.1 |  | 4.8174 |  | 4.3174
2021-05-15 | 29.7417 | 30.0936 | 26.2962 | 24.5 | 25 | 25.5 | 26.7962 | 27.2962 | 3.4455 |  | 5.2417 |  | 4.7417 |  | 4.2417 |  | 2.9455 |  | 2.4455
2021-05-16 | 32.2167 | 30.0481 | 26.2835 | 24.5 | 25 | 25.5 | 26.7835 | 27.2835 | 5.9332 |  | 7.7167 |  | 7.2167 |  | 6.7167 |  | 5.4332 |  | 4.9332
2021-05-17 | 32.2208 | 30.2625 | 26.3435 | 24.5 | 25 | 25.5 | 26.8435 | 27.3435 | 5.8773 |  | 7.7208 |  | 7.2208 |  | 6.7208 |  | 5.3773 |  | 4.8773
2021-05-18 | 27.5458 | 30.5013 | 26.4104 | 24.5 | 25 | 25.5 | 26.9104 | 27.4104 | 1.1355 |  | 3.0458 |  | 2.5458 |  | 2.0458 |  | 0.63548 |  | 0.13548
2021-05-19 | 21.3833 | 30.4935 | 26.4082 | 24.5 | 25 | 25.5 | 26.9082 | 27.4082 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-05-20 | 26.7583 | 30.2113 | 26.3292 | 24.5 | 25 | 25.5 | 26.8292 | 27.3292 | 0.42918 |  | 2.2583 |  | 1.7583 |  | 1.2583 |  | 0 |  | 0
2021-05-21 | 27.975 | 30.2167 | 26.3307 | 24.5 | 25 | 25.5 | 26.8307 | 27.3307 | 1.6443 |  | 3.475 |  | 2.975 |  | 2.475 |  | 1.1443 |  | 0.64433
2021-05-22 | 27.35 | 30.3651 | 26.3722 | 24.5 | 25 | 25.5 | 26.8722 | 27.3722 | 0.97776 |  | 2.85 |  | 2.35 |  | 1.85 |  | 0.47776 |  | 0
2021-05-23 | 28.075 | 30.3649 | 26.3722 | 24.5 | 25 | 25.5 | 26.8722 | 27.3722 | 1.7028 |  | 3.575 |  | 3.075 |  | 2.575 |  | 1.2028 |  | 0.70284
2021-05-24 | 30.1667 | 30.3704 | 26.3737 | 24.5 | 25 | 25.5 | 26.8737 | 27.3737 | 3.793 |  | 5.6667 |  | 5.1667 |  | 4.6667 |  | 3.293 |  | 2.793
2021-05-25 | 32.1792 | 30.5043 | 26.4112 | 24.5 | 25 | 25.5 | 26.9112 | 27.4112 | 5.768 |  | 7.6792 |  | 7.1792 |  | 6.6792 |  | 5.268 |  | 4.768
2021-05-26 | 33.6125 | 30.6389 | 26.4489 | 24.5 | 25 | 25.5 | 26.9489 | 27.4489 | 7.1636 |  | 9.1125 |  | 8.6125 |  | 8.1125 |  | 6.6636 |  | 6.1636
2021-05-27 | 33.8125 | 30.7397 | 26.4771 | 24.5 | 25 | 25.5 | 26.9771 | 27.4771 | 7.3354 |  | 9.3125 |  | 8.8125 |  | 8.3125 |  | 6.8354 |  | 6.3354
2021-05-28 | 35.2458 | 30.774 | 26.4867 | 24.5 | 25 | 25.5 | 26.9867 | 27.4867 | 8.7591 |  | 10.7458 |  | 10.2458 |  | 9.7458 |  | 8.2591 |  | 7.7591
2021-05-29 | 34.6542 | 30.8269 | 26.5015 | 24.5 | 25 | 25.5 | 27.0015 | 27.5015 | 8.1526 |  | 10.1542 |  | 9.6542 |  | 9.1542 |  | 7.6526 |  | 7.1526
2021-05-30 | 32.4375 | 30.8504 | 26.5081 | 24.5 | 25 | 25.5 | 27.0081 | 27.5081 | 5.9294 |  | 7.9375 |  | 7.4375 |  | 6.9375 |  | 5.4294 |  | 4.9294
2021-05-31 | 34.5542 | 30.7719 | 26.4861 | 24.5 | 25 | 25.5 | 26.9861 | 27.4861 | 8.068 |  | 10.0542 |  | 9.5542 |  | 9.0542 |  | 7.568 |  | 7.068
2021-06-01 | 25.8208 | 30.8356 | 26.504 | 24.5 | 25 | 25.5 | 27.004 | 27.504 | 0 |  | 1.3208 |  | 0.82083 |  | 0.32083 |  | 0 |  | 0
2021-06-02 | 25.8833 | 30.6576 | 26.4541 | 24.5 | 25 | 25.5 | 26.9541 | 27.4541 | 0 |  | 1.3833 |  | 0.88333 |  | 0.38333 |  | 0 |  | 0
2021-06-03 | 30.4792 | 30.4578 | 26.3982 | 24.5 | 25 | 25.5 | 26.8982 | 27.3982 | 4.081 |  | 5.9792 |  | 5.4792 |  | 4.9792 |  | 3.581 |  | 3.081
2021-06-04 | 32.6375 | 30.3857 | 26.378 | 24.5 | 25 | 25.5 | 26.878 | 27.378 | 6.2595 |  | 8.1375 |  | 7.6375 |  | 7.1375 |  | 5.7595 |  | 5.2595
2021-06-05 | 30.0542 | 30.3776 | 26.3757 | 24.5 | 25 | 25.5 | 26.8757 | 27.3757 | 3.6784 |  | 5.5542 |  | 5.0542 |  | 4.5542 |  | 3.1784 |  | 2.6784
2021-06-06 | 31.5917 | 30.3974 | 26.3813 | 24.5 | 25 | 25.5 | 26.8813 | 27.3813 | 5.2104 |  | 7.0917 |  | 6.5917 |  | 6.0917 |  | 4.7104 |  | 4.2104
2021-06-07 | 34.7 | 30.4967 | 26.4091 | 24.5 | 25 | 25.5 | 26.9091 | 27.4091 | 8.2909 |  | 10.2 |  | 9.7 |  | 9.2 |  | 7.7909 |  | 7.2909
2021-06-08 | 36.0958 | 30.5993 | 26.4378 | 24.5 | 25 | 25.5 | 26.9378 | 27.4378 | 9.658 |  | 11.5958 |  | 11.0958 |  | 10.5958 |  | 9.158 |  | 8.658
2021-06-09 | 36.4167 | 30.7003 | 26.4661 | 24.5 | 25 | 25.5 | 26.9661 | 27.4661 | 9.9506 |  | 11.9167 |  | 11.4167 |  | 10.9167 |  | 9.4506 |  | 8.9506
2021-06-10 | 36.6542 | 30.8888 | 26.5189 | 24.5 | 25 | 25.5 | 27.0189 | 27.5189 | 10.1353 |  | 12.1542 |  | 11.6542 |  | 11.1542 |  | 9.6353 |  | 9.1353
2021-06-11 | 35.4167 | 31.0603 | 26.5669 | 24.5 | 25 | 25.5 | 27.0669 | 27.5669 | 8.8498 |  | 10.9167 |  | 10.4167 |  | 9.9167 |  | 8.3498 |  | 7.8498
2021-06-12 | 34.7958 | 31.2357 | 26.616 | 24.5 | 25 | 25.5 | 27.116 | 27.616 | 8.1798 |  | 10.2958 |  | 9.7958 |  | 9.2958 |  | 7.6798 |  | 7.1798
2021-06-13 | 28.7792 | 31.4025 | 26.6627 | 24.5 | 25 | 25.5 | 27.1627 | 27.6627 | 2.1165 |  | 4.2792 |  | 3.7792 |  | 3.2792 |  | 1.6165 |  | 1.1165
2021-06-14 | 33.0125 | 31.3085 | 26.6364 | 24.5 | 25 | 25.5 | 27.1364 | 27.6364 | 6.3761 |  | 8.5125 |  | 8.0125 |  | 7.5125 |  | 5.8761 |  | 5.3761
2021-06-15 | 29.7375 | 31.4175 | 26.6669 | 24.5 | 25 | 25.5 | 27.1669 | 27.6669 | 3.0706 |  | 5.2375 |  | 4.7375 |  | 4.2375 |  | 2.5706 |  | 2.0706
2021-06-16 | 28.7375 | 31.3349 | 26.6438 | 24.5 | 25 | 25.5 | 27.1438 | 27.6438 | 2.0937 |  | 4.2375 |  | 3.7375 |  | 3.2375 |  | 1.5937 |  | 1.0937
2021-06-17 | 31.8208 | 31.2188 | 26.6113 | 24.5 | 25 | 25.5 | 27.1113 | 27.6113 | 5.2096 |  | 7.3208 |  | 6.8208 |  | 6.3208 |  | 4.7096 |  | 4.2096
2021-06-18 | 32.3208 | 31.3613 | 26.6512 | 24.5 | 25 | 25.5 | 27.1512 | 27.6512 | 5.6697 |  | 7.8208 |  | 7.3208 |  | 6.8208 |  | 5.1697 |  | 4.6697
2021-06-19 | 31.325 | 31.7258 | 26.7532 | 24.5 | 25 | 25.5 | 27.2532 | 27.7532 | 4.5718 |  | 6.825 |  | 6.325 |  | 5.825 |  | 4.0718 |  | 3.5718
2021-06-20 | 31.9708 | 31.8781 | 26.7959 | 24.5 | 25 | 25.5 | 27.2959 | 27.7959 | 5.175 |  | 7.4708 |  | 6.9708 |  | 6.4708 |  | 4.675 |  | 4.175
2021-06-21 | 32.2333 | 32.0113 | 26.8332 | 24.5 | 25 | 25.5 | 27.3332 | 27.8332 | 5.4002 |  | 7.7333 |  | 7.2333 |  | 6.7333 |  | 4.9002 |  | 4.4002
2021-06-22 | 33.7125 | 32.174 | 26.8787 | 24.5 | 25 | 25.5 | 27.3787 | 27.8787 | 6.8338 |  | 9.2125 |  | 8.7125 |  | 8.2125 |  | 6.3338 |  | 5.8338
2021-06-23 | 35.0333 | 32.3619 | 26.9313 | 24.5 | 25 | 25.5 | 27.4313 | 27.9313 | 8.102 |  | 10.5333 |  | 10.0333 |  | 9.5333 |  | 7.602 |  | 7.102
2021-06-24 | 31.4042 | 32.5242 | 26.9768 | 24.5 | 25 | 25.5 | 27.4768 | 27.9768 | 4.4274 |  | 6.9042 |  | 6.4042 |  | 5.9042 |  | 3.9274 |  | 3.4274
2021-06-25 | 29.8833 | 32.4983 | 26.9695 | 24.5 | 25 | 25.5 | 27.4695 | 27.9695 | 2.9138 |  | 5.3833 |  | 4.8833 |  | 4.3833 |  | 2.4138 |  | 1.9138
2021-06-26 | 30.625 | 32.374 | 26.9347 | 24.5 | 25 | 25.5 | 27.4347 | 27.9347 | 3.6903 |  | 6.125 |  | 5.625 |  | 5.125 |  | 3.1903 |  | 2.6903
2021-06-27 | 33.5208 | 32.2678 | 26.905 | 24.5 | 25 | 25.5 | 27.405 | 27.905 | 6.6159 |  | 9.0208 |  | 8.5208 |  | 8.0208 |  | 6.1159 |  | 5.6159
2021-06-28 | 35.0083 | 32.2103 | 26.8889 | 24.5 | 25 | 25.5 | 27.3889 | 27.8889 | 8.1195 |  | 10.5083 |  | 10.0083 |  | 9.5083 |  | 7.6195 |  | 7.1195
2021-06-29 | 36.4292 | 32.2221 | 26.8922 | 24.5 | 25 | 25.5 | 27.3922 | 27.8922 | 9.537 |  | 11.9292 |  | 11.4292 |  | 10.9292 |  | 9.037 |  | 8.537
2021-06-30 | 36.7875 | 32.3551 | 26.9294 | 24.5 | 25 | 25.5 | 27.4294 | 27.9294 | 9.8581 |  | 12.2875 |  | 11.7875 |  | 11.2875 |  | 9.3581 |  | 8.8581
2021-07-01 | 36.1958 | 32.4296 | 26.9503 | 24.5 | 25 | 25.5 | 27.4503 | 27.9503 | 9.2455 |  | 11.6958 |  | 11.1958 |  | 10.6958 |  | 8.7455 |  | 8.2455
2021-07-02 | 34.9917 | 32.7754 | 27.0471 | 24.5 | 25 | 25.5 | 27.5471 | 28.0471 | 7.9446 |  | 10.4917 |  | 9.9917 |  | 9.4917 |  | 7.4446 |  | 6.9446
2021-07-03 | 32.9917 | 33.079 | 27.1321 | 24.5 | 25 | 25.5 | 27.6321 | 28.1321 | 5.8595 |  | 8.4917 |  | 7.9917 |  | 7.4917 |  | 5.3595 |  | 4.8595
2021-07-04 | 32.675 | 33.1628 | 27.1556 | 24.5 | 25 | 25.5 | 27.6556 | 28.1556 | 5.5194 |  | 8.175 |  | 7.675 |  | 7.175 |  | 5.0194 |  | 4.5194
2021-07-05 | 31.2958 | 33.164 | 27.1559 | 24.5 | 25 | 25.5 | 27.6559 | 28.1559 | 4.1399 |  | 6.7958 |  | 6.2958 |  | 5.7958 |  | 3.6399 |  | 3.1399
2021-07-06 | 33.7167 | 33.2054 | 27.1675 | 24.5 | 25 | 25.5 | 27.6675 | 28.1675 | 6.5492 |  | 9.2167 |  | 8.7167 |  | 8.2167 |  | 6.0492 |  | 5.5492
2021-07-07 | 33.6875 | 33.2762 | 27.1874 | 24.5 | 25 | 25.5 | 27.6874 | 28.1874 | 6.5001 |  | 9.1875 |  | 8.6875 |  | 8.1875 |  | 6.0001 |  | 5.5001
2021-07-08 | 35.3833 | 33.2425 | 27.1779 | 24.5 | 25 | 25.5 | 27.6779 | 28.1779 | 8.2054 |  | 10.8833 |  | 10.3833 |  | 9.8833 |  | 7.7054 |  | 7.2054
2021-07-09 | 34.95 | 33.2187 | 27.1713 | 24.5 | 25 | 25.5 | 27.6713 | 28.1713 | 7.7788 |  | 10.45 |  | 9.95 |  | 9.45 |  | 7.2788 |  | 6.7788
2021-07-10 | 35.15 | 33.1699 | 27.1576 | 24.5 | 25 | 25.5 | 27.6576 | 28.1576 | 7.9924 |  | 10.65 |  | 10.15 |  | 9.65 |  | 7.4924 |  | 6.9924
2021-07-11 | 34.8625 | 33.1197 | 27.1435 | 24.5 | 25 | 25.5 | 27.6435 | 28.1435 | 7.719 |  | 10.3625 |  | 9.8625 |  | 9.3625 |  | 7.219 |  | 6.719
2021-07-12 | 32.2708 | 33.1012 | 27.1383 | 24.5 | 25 | 25.5 | 27.6383 | 28.1383 | 5.1325 |  | 7.7708 |  | 7.2708 |  | 6.7708 |  | 4.6325 |  | 4.1325
2021-07-13 | 29.0458 | 33.0171 | 27.1148 | 24.5 | 25 | 25.5 | 27.6148 | 28.1148 | 1.931 |  | 4.5458 |  | 4.0458 |  | 3.5458 |  | 1.431 |  | 0.93105
2021-07-14 | 26.8875 | 33.026 | 27.1173 | 24.5 | 25 | 25.5 | 27.6173 | 28.1173 | 0 |  | 2.3875 |  | 1.8875 |  | 1.3875 |  | 0 |  | 0
2021-07-15 | 29.1583 | 32.8218 | 27.0601 | 24.5 | 25 | 25.5 | 27.5601 | 28.0601 | 2.0982 |  | 4.6583 |  | 4.1583 |  | 3.6583 |  | 1.5982 |  | 1.0982
2021-07-16 | 32.6083 | 32.8025 | 27.0547 | 24.5 | 25 | 25.5 | 27.5547 | 28.0547 | 5.5536 |  | 8.1083 |  | 7.6083 |  | 7.1083 |  | 5.0536 |  | 4.5536
2021-07-17 | 33.7167 | 32.9315 | 27.0908 | 24.5 | 25 | 25.5 | 27.5908 | 28.0908 | 6.6258 |  | 9.2167 |  | 8.7167 |  | 8.2167 |  | 6.1258 |  | 5.6258
2021-07-18 | 32.0417 | 32.9947 | 27.1085 | 24.5 | 25 | 25.5 | 27.6085 | 28.1085 | 4.9331 |  | 7.5417 |  | 7.0417 |  | 6.5417 |  | 4.4331 |  | 3.9331
2021-07-19 | 27.5667 | 32.9854 | 27.1059 | 24.5 | 25 | 25.5 | 27.6059 | 28.1059 | 0.46075 |  | 3.0667 |  | 2.5667 |  | 2.0667 |  | 0 |  | 0
2021-07-20 | 30.5792 | 32.8601 | 27.0708 | 24.5 | 25 | 25.5 | 27.5708 | 28.0708 | 3.5083 |  | 6.0792 |  | 5.5792 |  | 5.0792 |  | 3.0083 |  | 2.5083
2021-07-21 | 30.9083 | 32.8137 | 27.0579 | 24.5 | 25 | 25.5 | 27.5579 | 28.0579 | 3.8505 |  | 6.4083 |  | 5.9083 |  | 5.4083 |  | 3.3505 |  | 2.8505
2021-07-22 | 29.8917 | 32.7696 | 27.0455 | 24.5 | 25 | 25.5 | 27.5455 | 28.0455 | 2.8462 |  | 5.3917 |  | 4.8917 |  | 4.3917 |  | 2.3462 |  | 1.8462
2021-07-23 | 30.4625 | 32.6422 | 27.0098 | 24.5 | 25 | 25.5 | 27.5098 | 28.0098 | 3.4527 |  | 5.9625 |  | 5.4625 |  | 4.9625 |  | 2.9527 |  | 2.4527
2021-07-24 | 32.1875 | 32.4899 | 26.9672 | 24.5 | 25 | 25.5 | 27.4672 | 27.9672 | 5.2203 |  | 7.6875 |  | 7.1875 |  | 6.6875 |  | 4.7203 |  | 4.2203
2021-07-25 | 33.8583 | 32.516 | 26.9745 | 24.5 | 25 | 25.5 | 27.4745 | 27.9745 | 6.8839 |  | 9.3583 |  | 8.8583 |  | 8.3583 |  | 6.3839 |  | 5.8839
2021-07-26 | 32.0708 | 32.6485 | 27.0116 | 24.5 | 25 | 25.5 | 27.5116 | 28.0116 | 5.0593 |  | 7.5708 |  | 7.0708 |  | 6.5708 |  | 4.5593 |  | 4.0593
2021-07-27 | 29.1875 | 32.6967 | 27.0251 | 24.5 | 25 | 25.5 | 27.5251 | 28.0251 | 2.1624 |  | 4.6875 |  | 4.1875 |  | 3.6875 |  | 1.6624 |  | 1.1624
2021-07-28 | 27.0958 | 32.5522 | 26.9846 | 24.5 | 25 | 25.5 | 27.4846 | 27.9846 | 0.11121 |  | 2.5958 |  | 2.0958 |  | 1.5958 |  | 0 |  | 0
2021-07-29 | 28.075 | 32.2885 | 26.9108 | 24.5 | 25 | 25.5 | 27.4108 | 27.9108 | 1.1642 |  | 3.575 |  | 3.075 |  | 2.575 |  | 0.66423 |  | 0.16423
2021-07-30 | 26.7125 | 32.01 | 26.8328 | 24.5 | 25 | 25.5 | 27.3328 | 27.8328 | 0 |  | 2.2125 |  | 1.7125 |  | 1.2125 |  | 0 |  | 0
2021-07-31 | 28.2958 | 31.6742 | 26.7388 | 24.5 | 25 | 25.5 | 27.2388 | 27.7388 | 1.5571 |  | 3.7958 |  | 3.2958 |  | 2.7958 |  | 1.0571 |  | 0.55707
2021-08-01 | 29.7917 | 31.4108 | 26.665 | 24.5 | 25 | 25.5 | 27.165 | 27.665 | 3.1266 |  | 5.2917 |  | 4.7917 |  | 4.2917 |  | 2.6266 |  | 2.1266
2021-08-02 | 28.8625 | 31.2375 | 26.6165 | 24.5 | 25 | 25.5 | 27.1165 | 27.6165 | 2.246 |  | 4.3625 |  | 3.8625 |  | 3.3625 |  | 1.746 |  | 1.246
2021-08-03 | 28.3792 | 31.0999 | 26.578 | 24.5 | 25 | 25.5 | 27.078 | 27.578 | 1.8012 |  | 3.8792 |  | 3.3792 |  | 2.8792 |  | 1.3012 |  | 0.80121
2021-08-04 | 29.8792 | 30.9567 | 26.5379 | 24.5 | 25 | 25.5 | 27.0379 | 27.5379 | 3.3413 |  | 5.3792 |  | 4.8792 |  | 4.3792 |  | 2.8413 |  | 2.3413
2021-08-05 | 30.1 | 30.9094 | 26.5246 | 24.5 | 25 | 25.5 | 27.0246 | 27.5246 | 3.5754 |  | 5.6 |  | 5.1 |  | 4.6 |  | 3.0754 |  | 2.5754
2021-08-06 | 29.9042 | 30.7889 | 26.4909 | 24.5 | 25 | 25.5 | 26.9909 | 27.4909 | 3.4133 |  | 5.4042 |  | 4.9042 |  | 4.4042 |  | 2.9133 |  | 2.4133
2021-08-07 | 29.1958 | 30.6628 | 26.4556 | 24.5 | 25 | 25.5 | 26.9556 | 27.4556 | 2.7403 |  | 4.6958 |  | 4.1958 |  | 3.6958 |  | 2.2403 |  | 1.7403
2021-08-08 | 30.1625 | 30.4565 | 26.3978 | 24.5 | 25 | 25.5 | 26.8978 | 27.3978 | 3.7647 |  | 5.6625 |  | 5.1625 |  | 4.6625 |  | 3.2647 |  | 2.7647
2021-08-09 | 29.8792 | 30.2969 | 26.3531 | 24.5 | 25 | 25.5 | 26.8531 | 27.3531 | 3.526 |  | 5.3792 |  | 4.8792 |  | 4.3792 |  | 3.026 |  | 2.526
2021-08-10 | 30.9625 | 30.1213 | 26.304 | 24.5 | 25 | 25.5 | 26.804 | 27.304 | 4.6585 |  | 6.4625 |  | 5.9625 |  | 5.4625 |  | 4.1585 |  | 3.6585
2021-08-11 | 30.8708 | 29.9913 | 26.2675 | 24.5 | 25 | 25.5 | 26.7675 | 27.2675 | 4.6033 |  | 6.3708 |  | 5.8708 |  | 5.3708 |  | 4.1033 |  | 3.6033
2021-08-12 | 31.0375 | 29.9446 | 26.2545 | 24.5 | 25 | 25.5 | 26.7545 | 27.2545 | 4.783 |  | 6.5375 |  | 6.0375 |  | 5.5375 |  | 4.283 |  | 3.783
2021-08-13 | 31.5 | 30.011 | 26.2731 | 24.5 | 25 | 25.5 | 26.7731 | 27.2731 | 5.2269 |  | 7 |  | 6.5 |  | 6 |  | 4.7269 |  | 4.2269
2021-08-14 | 31.1792 | 30.1647 | 26.3161 | 24.5 | 25 | 25.5 | 26.8161 | 27.3161 | 4.863 |  | 6.6792 |  | 6.1792 |  | 5.6792 |  | 4.363 |  | 3.863
2021-08-15 | 31.0958 | 30.2321 | 26.335 | 24.5 | 25 | 25.5 | 26.835 | 27.335 | 4.7608 |  | 6.5958 |  | 6.0958 |  | 5.5958 |  | 4.2608 |  | 3.7608
2021-08-16 | 31.7333 | 30.1817 | 26.3209 | 24.5 | 25 | 25.5 | 26.8209 | 27.3209 | 5.4125 |  | 7.2333 |  | 6.7333 |  | 6.2333 |  | 4.9125 |  | 4.4125
2021-08-17 | 32.5917 | 30.1156 | 26.3024 | 24.5 | 25 | 25.5 | 26.8024 | 27.3024 | 6.2893 |  | 8.0917 |  | 7.5917 |  | 7.0917 |  | 5.7893 |  | 5.2893
2021-08-18 | 33.3208 | 30.1339 | 26.3075 | 24.5 | 25 | 25.5 | 26.8075 | 27.3075 | 7.0133 |  | 8.8208 |  | 8.3208 |  | 7.8208 |  | 6.5133 |  | 6.0133
2021-08-19 | 33.2667 | 30.3257 | 26.3612 | 24.5 | 25 | 25.5 | 26.8612 | 27.3612 | 6.9055 |  | 8.7667 |  | 8.2667 |  | 7.7667 |  | 6.4055 |  | 5.9055
2021-08-20 | 30.7333 | 30.4153 | 26.3863 | 24.5 | 25 | 25.5 | 26.8863 | 27.3863 | 4.3471 |  | 6.2333 |  | 5.7333 |  | 5.2333 |  | 3.8471 |  | 3.3471
2021-08-21 | 26.9583 | 30.4094 | 26.3846 | 24.5 | 25 | 25.5 | 26.8846 | 27.3846 | 0.57369 |  | 2.4583 |  | 1.9583 |  | 1.4583 |  | 0.073689 |  | 0
2021-08-22 | 27.3875 | 30.3117 | 26.3573 | 24.5 | 25 | 25.5 | 26.8573 | 27.3573 | 1.0302 |  | 2.8875 |  | 2.3875 |  | 1.8875 |  | 0.53023 |  | 0.030233
2021-08-23 | 29.2875 | 30.2092 | 26.3286 | 24.5 | 25 | 25.5 | 26.8286 | 27.3286 | 2.9589 |  | 4.7875 |  | 4.2875 |  | 3.7875 |  | 2.4589 |  | 1.9589
2021-08-24 | 31.7583 | 30.1125 | 26.3015 | 24.5 | 25 | 25.5 | 26.8015 | 27.3015 | 5.4568 |  | 7.2583 |  | 6.7583 |  | 6.2583 |  | 4.9568 |  | 4.4568
2021-08-25 | 32.225 | 30.0425 | 26.2819 | 24.5 | 25 | 25.5 | 26.7819 | 27.2819 | 5.9431 |  | 7.725 |  | 7.225 |  | 6.725 |  | 5.4431 |  | 4.9431
2021-08-26 | 30.4875 | 30.0476 | 26.2833 | 24.5 | 25 | 25.5 | 26.7833 | 27.2833 | 4.2042 |  | 5.9875 |  | 5.4875 |  | 4.9875 |  | 3.7042 |  | 3.2042
2021-08-27 | 31.0875 | 30.091 | 26.2955 | 24.5 | 25 | 25.5 | 26.7955 | 27.2955 | 4.792 |  | 6.5875 |  | 6.0875 |  | 5.5875 |  | 4.292 |  | 3.792
2021-08-28 | 31.7375 | 30.224 | 26.3327 | 24.5 | 25 | 25.5 | 26.8327 | 27.3327 | 5.4048 |  | 7.2375 |  | 6.7375 |  | 6.2375 |  | 4.9048 |  | 4.4048
2021-08-29 | 31.3583 | 30.3461 | 26.3669 | 24.5 | 25 | 25.5 | 26.8669 | 27.3669 | 4.9914 |  | 6.8583 |  | 6.3583 |  | 5.8583 |  | 4.4914 |  | 3.9914
2021-08-30 | 30.1708 | 30.501 | 26.4103 | 24.5 | 25 | 25.5 | 26.9103 | 27.4103 | 3.7606 |  | 5.6708 |  | 5.1708 |  | 4.6708 |  | 3.2606 |  | 2.7606
2021-08-31 | 26.6875 | 30.5635 | 26.4278 | 24.5 | 25 | 25.5 | 26.9278 | 27.4278 | 0.25973 |  | 2.1875 |  | 1.6875 |  | 1.1875 |  | 0 |  | 0
2021-09-01 | 25.4583 | 30.46 | 26.3988 | 24.5 | 25 | 25.5 | 26.8988 | 27.3988 | 0 |  | 0.95833 |  | 0.45833 |  | 0 |  | 0 |  | 0
2021-09-02 | 27.0292 | 30.3465 | 26.367 | 24.5 | 25 | 25.5 | 26.867 | 27.367 | 0.66214 |  | 2.5292 |  | 2.0292 |  | 1.5292 |  | 0.16214 |  | 0
2021-09-03 | 26.7167 | 30.3015 | 26.3544 | 24.5 | 25 | 25.5 | 26.8544 | 27.3544 | 0.36224 |  | 2.2167 |  | 1.7167 |  | 1.2167 |  | 0 |  | 0
2021-09-04 | 27.875 | 30.1961 | 26.3249 | 24.5 | 25 | 25.5 | 26.8249 | 27.3249 | 1.5501 |  | 3.375 |  | 2.875 |  | 2.375 |  | 1.0501 |  | 0.55009
2021-09-05 | 27.8625 | 30.1219 | 26.3041 | 24.5 | 25 | 25.5 | 26.8041 | 27.3041 | 1.5584 |  | 3.3625 |  | 2.8625 |  | 2.3625 |  | 1.0584 |  | 0.55836
2021-09-06 | 30.3708 | 30.0539 | 26.2851 | 24.5 | 25 | 25.5 | 26.7851 | 27.2851 | 4.0857 |  | 5.8708 |  | 5.3708 |  | 4.8708 |  | 3.5857 |  | 3.0857
2021-09-07 | 30.0458 | 30.0931 | 26.2961 | 24.5 | 25 | 25.5 | 26.7961 | 27.2961 | 3.7498 |  | 5.5458 |  | 5.0458 |  | 4.5458 |  | 3.2498 |  | 2.7498
2021-09-08 | 29.1167 | 30.0892 | 26.295 | 24.5 | 25 | 25.5 | 26.795 | 27.295 | 2.8217 |  | 4.6167 |  | 4.1167 |  | 3.6167 |  | 2.3217 |  | 1.8217
2021-09-09 | 28.3667 | 30.0637 | 26.2878 | 24.5 | 25 | 25.5 | 26.7878 | 27.2878 | 2.0788 |  | 3.8667 |  | 3.3667 |  | 2.8667 |  | 1.5788 |  | 1.0788
2021-09-10 | 28.75 | 29.9772 | 26.2636 | 24.5 | 25 | 25.5 | 26.7636 | 27.2636 | 2.4864 |  | 4.25 |  | 3.75 |  | 3.25 |  | 1.9864 |  | 1.4864
2021-09-11 | 25.9375 | 29.9065 | 26.2438 | 24.5 | 25 | 25.5 | 26.7438 | 27.2438 | 0 |  | 1.4375 |  | 0.9375 |  | 0.4375 |  | 0 |  | 0
2021-09-12 | 27.2792 | 29.7365 | 26.1962 | 24.5 | 25 | 25.5 | 26.6962 | 27.1962 | 1.0829 |  | 2.7792 |  | 2.2792 |  | 1.7792 |  | 0.58294 |  | 0.082939
2021-09-13 | 26.6958 | 29.5958 | 26.1568 | 24.5 | 25 | 25.5 | 26.6568 | 27.1568 | 0.539 |  | 2.1958 |  | 1.6958 |  | 1.1958 |  | 0.039 |  | 0
2021-09-14 | 28.2042 | 29.4464 | 26.115 | 24.5 | 25 | 25.5 | 26.615 | 27.115 | 2.0892 |  | 3.7042 |  | 3.2042 |  | 2.7042 |  | 1.5892 |  | 1.0892
2021-09-15 | 29.7833 | 29.35 | 26.088 | 24.5 | 25 | 25.5 | 26.588 | 27.088 | 3.6953 |  | 5.2833 |  | 4.7833 |  | 4.2833 |  | 3.1953 |  | 2.6953
2021-09-16 | 27.9833 | 29.285 | 26.0698 | 24.5 | 25 | 25.5 | 26.5698 | 27.0698 | 1.9135 |  | 3.4833 |  | 2.9833 |  | 2.4833 |  | 1.4135 |  | 0.91353
2021-09-17 | 27.8083 | 29.1314 | 26.0268 | 24.5 | 25 | 25.5 | 26.5268 | 27.0268 | 1.7815 |  | 3.3083 |  | 2.8083 |  | 2.3083 |  | 1.2815 |  | 0.78154
2021-09-18 | 28.55 | 28.9476 | 25.9753 | 24.5 | 25 | 25.5 | 26.4753 | 26.9753 | 2.5747 |  | 4.05 |  | 3.55 |  | 3.05 |  | 2.0747 |  | 1.5747
2021-09-19 | 29.1833 | 28.7904 | 25.9313 | 24.5 | 25 | 25.5 | 26.4313 | 26.9313 | 3.252 |  | 4.6833 |  | 4.1833 |  | 3.6833 |  | 2.752 |  | 2.252
2021-09-20 | 29.0375 | 28.7387 | 25.9168 | 24.5 | 25 | 25.5 | 26.4168 | 26.9168 | 3.1207 |  | 4.5375 |  | 4.0375 |  | 3.5375 |  | 2.6207 |  | 2.1207
2021-09-21 | 28.525 | 28.8081 | 25.9363 | 24.5 | 25 | 25.5 | 26.4363 | 26.9363 | 2.5887 |  | 4.025 |  | 3.525 |  | 3.025 |  | 2.0887 |  | 1.5887
2021-09-22 | 25.7667 | 28.846 | 25.9469 | 24.5 | 25 | 25.5 | 26.4469 | 26.9469 | 0 |  | 1.2667 |  | 0.76667 |  | 0.26667 |  | 0 |  | 0
2021-09-23 | 25.9833 | 28.7286 | 25.914 | 24.5 | 25 | 25.5 | 26.414 | 26.914 | 0.069322 |  | 1.4833 |  | 0.98333 |  | 0.48333 |  | 0 |  | 0
2021-09-24 | 26.7167 | 28.5361 | 25.8601 | 24.5 | 25 | 25.5 | 26.3601 | 26.8601 | 0.85656 |  | 2.2167 |  | 1.7167 |  | 1.2167 |  | 0.35656 |  | 0
2021-09-25 | 28.0292 | 28.3525 | 25.8087 | 24.5 | 25 | 25.5 | 26.3087 | 26.8087 | 2.2205 |  | 3.5292 |  | 3.0292 |  | 2.5292 |  | 1.7205 |  | 1.2205
2021-09-26 | 27.9375 | 28.2706 | 25.7858 | 24.5 | 25 | 25.5 | 26.2858 | 26.7858 | 2.1517 |  | 3.4375 |  | 2.9375 |  | 2.4375 |  | 1.6517 |  | 1.1517
2021-09-27 | 28.4417 | 28.1656 | 25.7564 | 24.5 | 25 | 25.5 | 26.2564 | 26.7564 | 2.6853 |  | 3.9417 |  | 3.4417 |  | 2.9417 |  | 2.1853 |  | 1.6853
2021-09-28 | 29.4792 | 28.0557 | 25.7256 | 24.5 | 25 | 25.5 | 26.2256 | 26.7256 | 3.7536 |  | 4.9792 |  | 4.4792 |  | 3.9792 |  | 3.2536 |  | 2.7536
2021-09-29 | 29.2208 | 27.9931 | 25.7081 | 24.5 | 25 | 25.5 | 26.2081 | 26.7081 | 3.5128 |  | 4.7208 |  | 4.2208 |  | 3.7208 |  | 3.0128 |  | 2.5128
2021-09-30 | 29.2458 | 27.9614 | 25.6992 | 24.5 | 25 | 25.5 | 26.1992 | 26.6992 | 3.5466 |  | 4.7458 |  | 4.2458 |  | 3.7458 |  | 3.0466 |  | 2.5466
2021-10-01 | 29.7375 | 28.0467 | 25.7231 | 24.5 | 25 | 25.5 | 26.2231 | 26.7231 | 4.0144 |  | 5.2375 |  | 4.7375 |  | 4.2375 |  | 3.5144 |  | 3.0144
2021-10-02 | 29.0792 | 28.1893 | 25.763 | 24.5 | 25 | 25.5 | 26.263 | 26.763 | 3.3162 |  | 4.5792 |  | 4.0792 |  | 3.5792 |  | 2.8162 |  | 2.3162
2021-10-03 | 30.0083 | 28.2576 | 25.7821 | 24.5 | 25 | 25.5 | 26.2821 | 26.7821 | 4.2262 |  | 5.5083 |  | 5.0083 |  | 4.5083 |  | 3.7262 |  | 3.2262
2021-10-04 | 30.1417 | 28.3674 | 25.8129 | 24.5 | 25 | 25.5 | 26.3129 | 26.8129 | 4.3288 |  | 5.6417 |  | 5.1417 |  | 4.6417 |  | 3.8288 |  | 3.3288
2021-10-05 | 28.7625 | 28.4429 | 25.834 | 24.5 | 25 | 25.5 | 26.334 | 26.834 | 2.9285 |  | 4.2625 |  | 3.7625 |  | 3.2625 |  | 2.4285 |  | 1.9285
2021-10-06 | 29.0417 | 28.4729 | 25.8424 | 24.5 | 25 | 25.5 | 26.3424 | 26.8424 | 3.1993 |  | 4.5417 |  | 4.0417 |  | 3.5417 |  | 2.6993 |  | 2.1993
2021-10-07 | 28.2583 | 28.4286 | 25.83 | 24.5 | 25 | 25.5 | 26.33 | 26.83 | 2.4283 |  | 3.7583 |  | 3.2583 |  | 2.7583 |  | 1.9283 |  | 1.4283
2021-10-08 | 28.6417 | 28.369 | 25.8133 | 24.5 | 25 | 25.5 | 26.3133 | 26.8133 | 2.8283 |  | 4.1417 |  | 3.6417 |  | 3.1417 |  | 2.3283 |  | 1.8283
2021-10-09 | 29.2542 | 28.3532 | 25.8089 | 24.5 | 25 | 25.5 | 26.3089 | 26.8089 | 3.4453 |  | 4.7542 |  | 4.2542 |  | 3.7542 |  | 2.9453 |  | 2.4453
2021-10-10 | 28.8917 | 28.3828 | 25.8172 | 24.5 | 25 | 25.5 | 26.3172 | 26.8172 | 3.0745 |  | 4.3917 |  | 3.8917 |  | 3.3917 |  | 2.5745 |  | 2.0745
2021-10-11 | 29.1208 | 28.3875 | 25.8185 | 24.5 | 25 | 25.5 | 26.3185 | 26.8185 | 3.3023 |  | 4.6208 |  | 4.1208 |  | 3.6208 |  | 2.8023 |  | 2.3023
2021-10-12 | 27.9667 | 28.4936 | 25.8482 | 24.5 | 25 | 25.5 | 26.3482 | 26.8482 | 2.1185 |  | 3.4667 |  | 2.9667 |  | 2.4667 |  | 1.6185 |  | 1.1185
2021-10-13 | 26.4208 | 28.5165 | 25.8546 | 24.5 | 25 | 25.5 | 26.3546 | 26.8546 | 0.56621 |  | 1.9208 |  | 1.4208 |  | 0.92083 |  | 0.066206 |  | 0
2021-10-14 | 25.2625 | 28.5074 | 25.8521 | 24.5 | 25 | 25.5 | 26.3521 | 26.8521 | 0 |  | 0.7625 |  | 0.2625 |  | 0 |  | 0 |  | 0
2021-10-15 | 24.6708 | 28.4093 | 25.8246 | 24.5 | 25 | 25.5 | 26.3246 | 26.8246 | 0 |  | 0.17083 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-16 | 26.5792 | 28.2389 | 25.7769 | 24.5 | 25 | 25.5 | 26.2769 | 26.7769 | 0.80228 |  | 2.0792 |  | 1.5792 |  | 1.0792 |  | 0.30228 |  | 0
2021-10-17 | 25.375 | 28.1921 | 25.7638 | 24.5 | 25 | 25.5 | 26.2638 | 26.7638 | 0 |  | 0.875 |  | 0.375 |  | 0 |  | 0 |  | 0
2021-10-18 | 21.9917 | 28.111 | 25.7411 | 24.5 | 25 | 25.5 | 26.2411 | 26.7411 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-19 | 23.8375 | 27.8924 | 25.6799 | 24.5 | 25 | 25.5 | 26.1799 | 26.6799 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-20 | 25.025 | 27.7142 | 25.63 | 24.5 | 25 | 25.5 | 26.13 | 26.63 | 0 |  | 0.525 |  | 0.025 |  | 0 |  | 0 |  | 0
2021-10-21 | 25.6375 | 27.5804 | 25.5925 | 24.5 | 25 | 25.5 | 26.0925 | 26.5925 | 0.044983 |  | 1.1375 |  | 0.6375 |  | 0.1375 |  | 0 |  | 0
2021-10-22 | 25.3875 | 27.4842 | 25.5656 | 24.5 | 25 | 25.5 | 26.0656 | 26.5656 | 0 |  | 0.8875 |  | 0.3875 |  | 0 |  | 0 |  | 0
2021-10-23 | 24.6583 | 27.4715 | 25.562 | 24.5 | 25 | 25.5 | 26.062 | 26.562 | 0 |  | 0.15833 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-24 | 23.4833 | 27.4274 | 25.5497 | 24.5 | 25 | 25.5 | 26.0497 | 26.5497 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-25 | 22 | 27.3196 | 25.5195 | 24.5 | 25 | 25.5 | 26.0195 | 26.5195 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-26 | 21.25 | 27.1186 | 25.4632 | 24.5 | 25 | 25.5 | 25.9632 | 26.4632 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-27 | 21.6 | 26.8957 | 25.4008 | 24.5 | 25 | 25.5 | 25.9008 | 26.4008 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-28 | 21.6833 | 26.6676 | 25.3369 | 24.5 | 25 | 25.5 | 25.8369 | 26.3369 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-29 | 21.1708 | 26.4078 | 25.2642 | 24.5 | 25 | 25.5 | 25.7642 | 26.2642 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-30 | 21.2083 | 26.1394 | 25.189 | 24.5 | 25 | 25.5 | 25.689 | 26.189 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-10-31 | 21.8125 | 25.8715 | 25.114 | 24.5 | 25 | 25.5 | 25.614 | 26.114 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-01 | 23.2833 | 25.6074 | 25.0401 | 24.5 | 25 | 25.5 | 25.5401 | 26.0401 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-02 | 23.8583 | 25.4142 | 24.986 | 24.5 | 25 | 25.5 | 25.486 | 25.986 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-03 | 21.775 | 25.2092 | 24.9286 | 24.5 | 25 | 25.5 | 25.4286 | 25.9286 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-04 | 19.2375 | 24.9303 | 24.8505 | 24.5 | 25 | 25.5 | 25.3505 | 25.8505 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-05 | 19.6417 | 24.6128 | 24.7616 | 24.5 | 25 | 25.5 | 25.2616 | 25.7616 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-06 | 20.5917 | 24.2994 | 24.6738 | 24.5 | 25 | 25.5 | 25.1738 | 25.6738 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-07 | 20.1917 | 24.0439 | 24.6023 | 24.5 | 25 | 25.5 | 25.1023 | 25.6023 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-08 | 20.5083 | 23.7622 | 24.5234 | 24.5 | 25 | 25.5 | 25.0234 | 25.5234 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-09 | 20.7042 | 23.4707 | 24.4418 | 24.5 | 25 | 25.5 | 24.9418 | 25.4418 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-10 | 21.2375 | 23.1978 | 24.3654 | 24.5 | 25 | 25.5 | 24.8654 | 25.3654 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-11 | 21.3083 | 22.935 | 24.2918 | 24.5 | 25 | 25.5 | 24.7918 | 25.2918 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-12 | 18.9833 | 22.7131 | 24.2297 | 24.5 | 25 | 25.5 | 24.7297 | 25.2297 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-13 | 18.7292 | 22.4651 | 24.1602 | 24.5 | 25 | 25.5 | 24.6602 | 25.1602 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-14 | 17.8208 | 22.2474 | 24.0993 | 24.5 | 25 | 25.5 | 24.5993 | 25.0993 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-15 | 17.6875 | 22.019 | 24.0353 | 24.5 | 25 | 25.5 | 24.5353 | 25.0353 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-16 | 16.8833 | 21.7226 | 23.9523 | 24.5 | 25 | 25.5 | 24.4523 | 24.9523 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-17 | 16.8083 | 21.4396 | 23.8731 | 24.5 | 25 | 25.5 | 24.3731 | 24.8731 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-18 | 16.65 | 21.2668 | 23.8247 | 24.5 | 25 | 25.5 | 24.3247 | 24.8247 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-19 | 16.6833 | 21.0272 | 23.7576 | 24.5 | 25 | 25.5 | 24.2576 | 24.7576 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-20 | 19.0375 | 20.7492 | 23.6798 | 24.5 | 25 | 25.5 | 24.1798 | 24.6798 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-21 | 18.2292 | 20.5292 | 23.6182 | 24.5 | 25 | 25.5 | 24.1182 | 24.6182 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-22 | 17.3542 | 20.2906 | 23.5514 | 24.5 | 25 | 25.5 | 24.0514 | 24.5514 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-23 | 17.4458 | 20.0471 | 23.4832 | 24.5 | 25 | 25.5 | 23.9832 | 24.4832 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-24 | 19.6167 | 19.8458 | 23.4268 | 24.5 | 25 | 25.5 | 23.9268 | 24.4268 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-25 | 19.4125 | 19.7664 | 23.4046 | 24.5 | 25 | 25.5 | 23.9046 | 24.4046 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-26 | 18.45 | 19.7051 | 23.3874 | 24.5 | 25 | 25.5 | 23.8874 | 24.3874 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-27 | 18.7583 | 19.6001 | 23.358 | 24.5 | 25 | 25.5 | 23.858 | 24.358 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-28 | 18.55 | 19.5026 | 23.3307 | 24.5 | 25 | 25.5 | 23.8307 | 24.3307 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-29 | 17.2125 | 19.4153 | 23.3063 | 24.5 | 25 | 25.5 | 23.8063 | 24.3063 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-11-30 | 16.6083 | 19.2821 | 23.269 | 24.5 | 25 | 25.5 | 23.769 | 24.269 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-01 | 16.2333 | 19.1086 | 23.2204 | 24.5 | 25 | 25.5 | 23.7204 | 24.2204 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-02 | 15.0167 | 18.8736 | 23.1546 | 24.5 | 25 | 25.5 | 23.6546 | 24.1546 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-03 | 15.5708 | 18.5789 | 23.0721 | 24.5 | 25 | 25.5 | 23.5721 | 24.0721 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-04 | 16.8625 | 18.3721 | 23.0142 | 24.5 | 25 | 25.5 | 23.5142 | 24.0142 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-05 | 17.6417 | 18.2929 | 22.992 | 24.5 | 25 | 25.5 | 23.492 | 23.992 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-06 | 17.6417 | 18.2262 | 22.9733 | 24.5 | 25 | 25.5 | 23.4733 | 23.9733 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-07 | 15.4167 | 18.1279 | 22.9458 | 24.5 | 25 | 25.5 | 23.4458 | 23.9458 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-08 | 14.6125 | 17.9688 | 22.9013 | 24.5 | 25 | 25.5 | 23.4013 | 23.9013 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-09 | 14.325 | 17.7722 | 22.8462 | 24.5 | 25 | 25.5 | 23.3462 | 23.8462 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-10 | 13.8917 | 17.5596 | 22.7867 | 24.5 | 25 | 25.5 | 23.2867 | 23.7867 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-11 | 13.3167 | 17.3147 | 22.7181 | 24.5 | 25 | 25.5 | 23.2181 | 23.7181 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-12 | 14.0917 | 17.0483 | 22.6435 | 24.5 | 25 | 25.5 | 23.1435 | 23.6435 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-13 | 13.6 | 16.8853 | 22.5979 | 24.5 | 25 | 25.5 | 23.0979 | 23.5979 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-14 | 13.9 | 16.7143 | 22.55 | 24.5 | 25 | 25.5 | 23.05 | 23.55 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-15 | 12.3625 | 16.5836 | 22.5134 | 24.5 | 25 | 25.5 | 23.0134 | 23.5134 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-16 | 11.725 | 16.4061 | 22.4637 | 24.5 | 25 | 25.5 | 22.9637 | 23.4637 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-17 | 9.7167 | 16.2342 | 22.4156 | 24.5 | 25 | 25.5 | 22.9156 | 23.4156 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-18 | 9.1625 | 15.9978 | 22.3494 | 24.5 | 25 | 25.5 | 22.8494 | 23.3494 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-19 | 9.4083 | 15.7482 | 22.2795 | 24.5 | 25 | 25.5 | 22.7795 | 23.2795 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-20 | 12.0458 | 15.5057 | 22.2116 | 24.5 | 25 | 25.5 | 22.7116 | 23.2116 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-21 | 13.8542 | 15.2726 | 22.1463 | 24.5 | 25 | 25.5 | 22.6463 | 23.1463 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-22 | 14.8542 | 15.1268 | 22.1055 | 24.5 | 25 | 25.5 | 22.6055 | 23.1055 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-23 | 15.6708 | 15.0435 | 22.0822 | 24.5 | 25 | 25.5 | 22.5822 | 23.0822 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-24 | 16.375 | 14.9843 | 22.0656 | 24.5 | 25 | 25.5 | 22.5656 | 23.0656 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-25 | 16.1833 | 14.8763 | 22.0354 | 24.5 | 25 | 25.5 | 22.5354 | 23.0354 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-26 | 16.0958 | 14.7686 | 22.0052 | 24.5 | 25 | 25.5 | 22.5052 | 23.0052 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-27 | 15.3583 | 14.6901 | 21.9832 | 24.5 | 25 | 25.5 | 22.4832 | 22.9832 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-28 | 14.4167 | 14.5768 | 21.9515 | 24.5 | 25 | 25.5 | 22.4515 | 22.9515 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-29 | 11.9542 | 14.439 | 21.9129 | 24.5 | 25 | 25.5 | 22.4129 | 22.9129 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-30 | 11.3333 | 14.2638 | 21.8639 | 24.5 | 25 | 25.5 | 22.3639 | 22.8639 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2021-12-31 | 11.2042 | 14.0879 | 21.8146 | 24.5 | 25 | 25.5 | 22.3146 | 22.8146 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## New Delhi
Date | Daywise mean temperature | Running mean temperature (RMT) | Neutral temperature_IMAC | Baseline temperature calculated from PMV model | Plant adjusted I (Baseline + 0.5°C) | Plant adjusted II (Baseline + 1°C) | Plant adjusted I+ IMAC | Plant adjusted II+ IMAC | ACDD based on IMAC neutral temperature | 833.0949 | ACDD based on baseline temperature i.e. 24.5 calculated from the PMV model | 1175.5208 | ACDD based on 0.5°C adjustment on baseline temperature because of plant | 1075.5583 | ACDD based on 1°C adjustment on baseline temperature because of plant | 978.1083 | ACDD based on IMAC neutral temperature considering 0.5°C plant effect | 732.5154 | ACDD based on IMAC neutral temperature considering 1°C plant effect | 634.7236
1990-01-01 | 12.8583 | 14.7043 | 21.9872 | 24.5 | 25 | 25.5 | 22.4872 | 22.9872 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-02 | 12.625 | 14.5857 | 21.954 | 24.5 | 25 | 25.5 | 22.454 | 22.954 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-03 | 13.5917 | 14.4578 | 21.9182 | 24.5 | 25 | 25.5 | 22.4182 | 22.9182 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-04 | 14.4417 | 14.3785 | 21.896 | 24.5 | 25 | 25.5 | 22.396 | 22.896 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-05 | 14.2083 | 14.3296 | 21.8823 | 24.5 | 25 | 25.5 | 22.3823 | 22.8823 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-06 | 14.7125 | 14.2725 | 21.8663 | 24.5 | 25 | 25.5 | 22.3663 | 22.8663 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-07 | 15.2375 | 14.2406 | 21.8574 | 24.5 | 25 | 25.5 | 22.3574 | 22.8574 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-08 | 14.9292 | 14.2303 | 21.8545 | 24.5 | 25 | 25.5 | 22.3545 | 22.8545 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-09 | 15.2167 | 14.2533 | 21.8609 | 24.5 | 25 | 25.5 | 22.3609 | 22.8609 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-10 | 16.4 | 14.321 | 21.8799 | 24.5 | 25 | 25.5 | 22.3799 | 22.8799 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-11 | 14.4708 | 14.4344 | 21.9116 | 24.5 | 25 | 25.5 | 22.4116 | 22.9116 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-12 | 15.3708 | 14.4642 | 21.92 | 24.5 | 25 | 25.5 | 22.42 | 22.92 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-13 | 15.8875 | 14.5085 | 21.9324 | 24.5 | 25 | 25.5 | 22.4324 | 22.9324 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-14 | 14.0542 | 14.5467 | 21.9431 | 24.5 | 25 | 25.5 | 22.4431 | 22.9431 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-15 | 13.6417 | 14.5411 | 21.9415 | 24.5 | 25 | 25.5 | 22.4415 | 22.9415 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-16 | 11.2792 | 14.4538 | 21.9171 | 24.5 | 25 | 25.5 | 22.4171 | 22.9171 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-17 | 13.0083 | 14.3032 | 21.8749 | 24.5 | 25 | 25.5 | 22.3749 | 22.8749 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-18 | 12.0625 | 14.2081 | 21.8483 | 24.5 | 25 | 25.5 | 22.3483 | 22.8483 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-19 | 10.9833 | 14.0762 | 21.8114 | 24.5 | 25 | 25.5 | 22.3114 | 22.8114 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-20 | 13.4625 | 13.9225 | 21.7683 | 24.5 | 25 | 25.5 | 22.2683 | 22.7683 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-21 | 13.4292 | 13.8397 | 21.7451 | 24.5 | 25 | 25.5 | 22.2451 | 22.7451 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-22 | 13.3667 | 13.7488 | 21.7197 | 24.5 | 25 | 25.5 | 22.2197 | 22.7197 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-23 | 13.5125 | 13.6763 | 21.6994 | 24.5 | 25 | 25.5 | 22.1994 | 22.6994 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-24 | 13.8542 | 13.5972 | 21.6772 | 24.5 | 25 | 25.5 | 22.1772 | 22.6772 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-25 | 13.7792 | 13.5604 | 21.6669 | 24.5 | 25 | 25.5 | 22.1669 | 22.6669 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-26 | 13.975 | 13.59 | 21.6752 | 24.5 | 25 | 25.5 | 22.1752 | 22.6752 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-27 | 13.9875 | 13.6389 | 21.6889 | 24.5 | 25 | 25.5 | 22.1889 | 22.6889 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-28 | 14.9292 | 13.7031 | 21.7069 | 24.5 | 25 | 25.5 | 22.2069 | 22.7069 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-29 | 15.2708 | 13.7872 | 21.7304 | 24.5 | 25 | 25.5 | 22.2304 | 22.7304 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-30 | 15.4333 | 13.8876 | 21.7585 | 24.5 | 25 | 25.5 | 22.2585 | 22.7585 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-31 | 15.6458 | 13.9993 | 21.7898 | 24.5 | 25 | 25.5 | 22.2898 | 22.7898 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-01 | 16.0292 | 14.0922 | 21.8158 | 24.5 | 25 | 25.5 | 22.3158 | 22.8158 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-02 | 14.6208 | 14.2057 | 21.8476 | 24.5 | 25 | 25.5 | 22.3476 | 22.8476 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-03 | 15.1417 | 14.24 | 21.8572 | 24.5 | 25 | 25.5 | 22.3572 | 22.8572 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-04 | 15.5167 | 14.2633 | 21.8637 | 24.5 | 25 | 25.5 | 22.3637 | 22.8637 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-05 | 17.3708 | 14.3069 | 21.8759 | 24.5 | 25 | 25.5 | 22.3759 | 22.8759 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-06 | 17.9625 | 14.3956 | 21.9008 | 24.5 | 25 | 25.5 | 22.4008 | 22.9008 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-07 | 18.5292 | 14.4864 | 21.9262 | 24.5 | 25 | 25.5 | 22.4262 | 22.9262 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-08 | 18.7708 | 14.6064 | 21.9598 | 24.5 | 25 | 25.5 | 22.4598 | 22.9598 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-09 | 20.0667 | 14.7249 | 21.993 | 24.5 | 25 | 25.5 | 22.493 | 22.993 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-10 | 18.7875 | 14.8471 | 22.0272 | 24.5 | 25 | 25.5 | 22.5272 | 23.0272 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-11 | 18.55 | 14.991 | 22.0675 | 24.5 | 25 | 25.5 | 22.5675 | 23.0675 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-12 | 17.3417 | 15.0969 | 22.0971 | 24.5 | 25 | 25.5 | 22.5971 | 23.0971 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-13 | 16.0667 | 15.1454 | 22.1107 | 24.5 | 25 | 25.5 | 22.6107 | 23.1107 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-14 | 14.9792 | 15.2125 | 22.1295 | 24.5 | 25 | 25.5 | 22.6295 | 23.1295 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-15 | 14.8583 | 15.2571 | 22.142 | 24.5 | 25 | 25.5 | 22.642 | 23.142 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-16 | 14.7167 | 15.3764 | 22.1754 | 24.5 | 25 | 25.5 | 22.6754 | 23.1754 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-17 | 16.1708 | 15.4333 | 22.1913 | 24.5 | 25 | 25.5 | 22.6913 | 23.1913 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-18 | 13.3917 | 15.5703 | 22.2297 | 24.5 | 25 | 25.5 | 22.7297 | 23.2297 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-19 | 15.1167 | 15.6506 | 22.2522 | 24.5 | 25 | 25.5 | 22.7522 | 23.2522 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-20 | 15.825 | 15.7057 | 22.2676 | 24.5 | 25 | 25.5 | 22.7676 | 23.2676 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-21 | 17.2125 | 15.7856 | 22.29 | 24.5 | 25 | 25.5 | 22.79 | 23.29 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-22 | 16.7792 | 15.9138 | 22.3259 | 24.5 | 25 | 25.5 | 22.8259 | 23.3259 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-23 | 18.2458 | 16.0226 | 22.3563 | 24.5 | 25 | 25.5 | 22.8563 | 23.3563 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-24 | 14.8 | 16.169 | 22.3973 | 24.5 | 25 | 25.5 | 22.8973 | 23.3973 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-25 | 16.6167 | 16.2031 | 22.4069 | 24.5 | 25 | 25.5 | 22.9069 | 23.4069 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-26 | 17.3417 | 16.2911 | 22.4315 | 24.5 | 25 | 25.5 | 22.9315 | 23.4315 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-27 | 16.2875 | 16.4029 | 22.4628 | 24.5 | 25 | 25.5 | 22.9628 | 23.4628 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-28 | 15.025 | 16.4482 | 22.4755 | 24.5 | 25 | 25.5 | 22.9755 | 23.4755 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-01 | 20.9542 | 16.44 | 22.4732 | 24.5 | 25 | 25.5 | 22.9732 | 23.4732 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-02 | 17.8125 | 16.624 | 22.5247 | 24.5 | 25 | 25.5 | 23.0247 | 23.5247 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-03 | 18.4083 | 16.6963 | 22.545 | 24.5 | 25 | 25.5 | 23.045 | 23.545 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-04 | 19.025 | 16.7756 | 22.5672 | 24.5 | 25 | 25.5 | 23.0672 | 23.5672 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-05 | 19.85 | 16.9224 | 22.6083 | 24.5 | 25 | 25.5 | 23.1083 | 23.6083 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-06 | 19.7833 | 17.0793 | 22.6522 | 24.5 | 25 | 25.5 | 23.1522 | 23.6522 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-07 | 20.6542 | 17.2215 | 22.692 | 24.5 | 25 | 25.5 | 23.192 | 23.692 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-08 | 21.6375 | 17.331 | 22.7227 | 24.5 | 25 | 25.5 | 23.2227 | 23.7227 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-09 | 22.0875 | 17.4535 | 22.757 | 24.5 | 25 | 25.5 | 23.257 | 23.757 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-10 | 21.1833 | 17.5721 | 22.7902 | 24.5 | 25 | 25.5 | 23.2902 | 23.7902 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-11 | 21.3958 | 17.6525 | 22.8127 | 24.5 | 25 | 25.5 | 23.3127 | 23.8127 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-12 | 21.4917 | 17.6968 | 22.8251 | 24.5 | 25 | 25.5 | 23.3251 | 23.8251 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-13 | 22.3833 | 17.7869 | 22.8503 | 24.5 | 25 | 25.5 | 23.3503 | 23.8503 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-14 | 20.9333 | 17.9147 | 22.8861 | 24.5 | 25 | 25.5 | 23.3861 | 23.8861 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-15 | 20.6208 | 18.0344 | 22.9196 | 24.5 | 25 | 25.5 | 23.4196 | 23.9196 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-16 | 21.4875 | 18.1862 | 22.9622 | 24.5 | 25 | 25.5 | 23.4622 | 23.9622 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-17 | 22.1792 | 18.4032 | 23.0229 | 24.5 | 25 | 25.5 | 23.5229 | 24.0229 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-18 | 23.0917 | 18.6472 | 23.0912 | 24.5 | 25 | 25.5 | 23.5912 | 24.0912 | 0.00044444 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-19 | 23.1333 | 18.9264 | 23.1694 | 24.5 | 25 | 25.5 | 23.6694 | 24.1694 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-20 | 24.1667 | 19.1585 | 23.2344 | 24.5 | 25 | 25.5 | 23.7344 | 24.2344 | 0.93229 |  | 0 |  | 0 |  | 0 |  | 0.43229 |  | 0
1990-03-21 | 24.5875 | 19.5176 | 23.3349 | 24.5 | 25 | 25.5 | 23.8349 | 24.3349 | 1.2526 |  | 0.0875 |  | 0 |  | 0 |  | 0.75256 |  | 0.25256
1990-03-22 | 25.8292 | 19.8333 | 23.4233 | 24.5 | 25 | 25.5 | 23.9233 | 24.4233 | 2.4058 |  | 1.3292 |  | 0.82917 |  | 0.32917 |  | 1.9058 |  | 1.4058
1990-03-23 | 24.5333 | 20.1668 | 23.5167 | 24.5 | 25 | 25.5 | 24.0167 | 24.5167 | 1.0166 |  | 0.033333 |  | 0 |  | 0 |  | 0.51663 |  | 0.016628
1990-03-24 | 23.9417 | 20.4108 | 23.585 | 24.5 | 25 | 25.5 | 24.085 | 24.585 | 0.35663 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-25 | 25.2167 | 20.6496 | 23.6519 | 24.5 | 25 | 25.5 | 24.1519 | 24.6519 | 1.5648 |  | 0.71667 |  | 0.21667 |  | 0 |  | 1.0648 |  | 0.56478
1990-03-26 | 24.7958 | 20.8819 | 23.7169 | 24.5 | 25 | 25.5 | 24.2169 | 24.7169 | 1.0789 |  | 0.29583 |  | 0 |  | 0 |  | 0.57889 |  | 0.078889
1990-03-27 | 21.8583 | 21.2151 | 23.8102 | 24.5 | 25 | 25.5 | 24.3102 | 24.8102 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-28 | 19.4625 | 21.3899 | 23.8592 | 24.5 | 25 | 25.5 | 24.3592 | 24.8592 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-29 | 20.625 | 21.4606 | 23.879 | 24.5 | 25 | 25.5 | 24.379 | 24.879 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-30 | 22.175 | 21.6051 | 23.9194 | 24.5 | 25 | 25.5 | 24.4194 | 24.9194 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-03-31 | 25.0042 | 21.8435 | 23.9862 | 24.5 | 25 | 25.5 | 24.4862 | 24.9862 | 1.018 |  | 0.50417 |  | 0.0041667 |  | 0 |  | 0.51799 |  | 0.017994
1990-04-01 | 23.9875 | 21.9785 | 24.024 | 24.5 | 25 | 25.5 | 24.524 | 25.024 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-04-02 | 24.6875 | 22.1843 | 24.0816 | 24.5 | 25 | 25.5 | 24.5816 | 25.0816 | 0.60589 |  | 0.1875 |  | 0 |  | 0 |  | 0.10589 |  | 0
1990-04-03 | 24.975 | 22.3936 | 24.1402 | 24.5 | 25 | 25.5 | 24.6402 | 25.1402 | 0.83479 |  | 0.475 |  | 0 |  | 0 |  | 0.33479 |  | 0
1990-04-04 | 26.7833 | 22.5919 | 24.1957 | 24.5 | 25 | 25.5 | 24.6957 | 25.1957 | 2.5876 |  | 2.2833 |  | 1.7833 |  | 1.2833 |  | 2.0876 |  | 1.5876
1990-04-05 | 26.4958 | 22.8231 | 24.2605 | 24.5 | 25 | 25.5 | 24.7605 | 25.2605 | 2.2354 |  | 1.9958 |  | 1.4958 |  | 0.99583 |  | 1.7354 |  | 1.2354
1990-04-06 | 27.0125 | 23.0468 | 24.3231 | 24.5 | 25 | 25.5 | 24.8231 | 25.3231 | 2.6894 |  | 2.5125 |  | 2.0125 |  | 1.5125 |  | 2.1894 |  | 1.6894
1990-04-07 | 25.2292 | 23.2587 | 24.3825 | 24.5 | 25 | 25.5 | 24.8825 | 25.3825 | 0.84672 |  | 0.72917 |  | 0.22917 |  | 0 |  | 0.34672 |  | 0
1990-04-08 | 26.5542 | 23.3785 | 24.416 | 24.5 | 25 | 25.5 | 24.916 | 25.416 | 2.1382 |  | 2.0542 |  | 1.5542 |  | 1.0542 |  | 1.6382 |  | 1.1382
1990-04-09 | 27.7333 | 23.5274 | 24.4577 | 24.5 | 25 | 25.5 | 24.9577 | 25.4577 | 3.2757 |  | 3.2333 |  | 2.7333 |  | 2.2333 |  | 2.7757 |  | 2.2757
1990-04-10 | 26.3625 | 23.7457 | 24.5188 | 24.5 | 25 | 25.5 | 25.0188 | 25.5188 | 1.8437 |  | 1.8625 |  | 1.3625 |  | 0.8625 |  | 1.3437 |  | 0.84371
1990-04-11 | 28.0208 | 23.9113 | 24.5652 | 24.5 | 25 | 25.5 | 25.0652 | 25.5652 | 3.4557 |  | 3.5208 |  | 3.0208 |  | 2.5208 |  | 2.9557 |  | 2.4557
1990-04-12 | 27.575 | 24.1289 | 24.6261 | 24.5 | 25 | 25.5 | 25.1261 | 25.6261 | 2.9489 |  | 3.075 |  | 2.575 |  | 2.075 |  | 2.4489 |  | 1.9489
1990-04-13 | 27.5875 | 24.3019 | 24.6745 | 24.5 | 25 | 25.5 | 25.1745 | 25.6745 | 2.913 |  | 3.0875 |  | 2.5875 |  | 2.0875 |  | 2.413 |  | 1.913
1990-04-14 | 28.6292 | 24.5238 | 24.7367 | 24.5 | 25 | 25.5 | 25.2367 | 25.7367 | 3.8925 |  | 4.1292 |  | 3.6292 |  | 3.1292 |  | 3.3925 |  | 2.8925
1990-04-15 | 28.0125 | 24.7907 | 24.8114 | 24.5 | 25 | 25.5 | 25.3114 | 25.8114 | 3.2011 |  | 3.5125 |  | 3.0125 |  | 2.5125 |  | 2.7011 |  | 2.2011
1990-04-16 | 27.8583 | 25.0082 | 24.8723 | 24.5 | 25 | 25.5 | 25.3723 | 25.8723 | 2.986 |  | 3.3583 |  | 2.8583 |  | 2.3583 |  | 2.486 |  | 1.986
1990-04-17 | 28.9125 | 25.1975 | 24.9253 | 24.5 | 25 | 25.5 | 25.4253 | 25.9253 | 3.9872 |  | 4.4125 |  | 3.9125 |  | 3.4125 |  | 3.4872 |  | 2.9872
1990-04-18 | 30.3542 | 25.3915 | 24.9796 | 24.5 | 25 | 25.5 | 25.4796 | 25.9796 | 5.3745 |  | 5.8542 |  | 5.3542 |  | 4.8542 |  | 4.8745 |  | 4.3745
1990-04-19 | 30.7833 | 25.6322 | 25.047 | 24.5 | 25 | 25.5 | 25.547 | 26.047 | 5.7363 |  | 6.2833 |  | 5.7833 |  | 5.2833 |  | 5.2363 |  | 4.7363
1990-04-20 | 31.7333 | 25.8528 | 25.1088 | 24.5 | 25 | 25.5 | 25.6088 | 26.1088 | 6.6246 |  | 7.2333 |  | 6.7333 |  | 6.2333 |  | 6.1246 |  | 5.6246
1990-04-21 | 29.225 | 26.091 | 25.1755 | 24.5 | 25 | 25.5 | 25.6755 | 26.1755 | 4.0495 |  | 4.725 |  | 4.225 |  | 3.725 |  | 3.5495 |  | 3.0495
1990-04-22 | 28.975 | 26.2042 | 25.2072 | 24.5 | 25 | 25.5 | 25.7072 | 26.2072 | 3.7678 |  | 4.475 |  | 3.975 |  | 3.475 |  | 3.2678 |  | 2.7678
1990-04-23 | 26.8875 | 26.3522 | 25.2486 | 24.5 | 25 | 25.5 | 25.7486 | 26.2486 | 1.6389 |  | 2.3875 |  | 1.8875 |  | 1.3875 |  | 1.1389 |  | 0.63888
1990-04-24 | 27.9875 | 26.4504 | 25.2761 | 24.5 | 25 | 25.5 | 25.7761 | 26.2761 | 2.7114 |  | 3.4875 |  | 2.9875 |  | 2.4875 |  | 2.2114 |  | 1.7114
1990-04-25 | 29.2208 | 26.5428 | 25.302 | 24.5 | 25 | 25.5 | 25.802 | 26.302 | 3.9189 |  | 4.7208 |  | 4.2208 |  | 3.7208 |  | 3.4189 |  | 2.9189
1990-04-26 | 30.1375 | 26.6903 | 25.3433 | 24.5 | 25 | 25.5 | 25.8433 | 26.3433 | 4.7942 |  | 5.6375 |  | 5.1375 |  | 4.6375 |  | 4.2942 |  | 3.7942
1990-04-27 | 30.9667 | 26.9663 | 25.4206 | 24.5 | 25 | 25.5 | 25.9206 | 26.4206 | 5.5461 |  | 6.4667 |  | 5.9667 |  | 5.4667 |  | 5.0461 |  | 4.5461
1990-04-28 | 32.0625 | 27.3497 | 25.5279 | 24.5 | 25 | 25.5 | 26.0279 | 26.5279 | 6.5346 |  | 7.5625 |  | 7.0625 |  | 6.5625 |  | 6.0346 |  | 5.5346
1990-04-29 | 31.5583 | 27.731 | 25.6347 | 24.5 | 25 | 25.5 | 26.1347 | 26.6347 | 5.9237 |  | 7.0583 |  | 6.5583 |  | 6.0583 |  | 5.4237 |  | 4.9237
1990-04-30 | 31.2667 | 28.0437 | 25.7223 | 24.5 | 25 | 25.5 | 26.2223 | 26.7223 | 5.5444 |  | 6.7667 |  | 6.2667 |  | 5.7667 |  | 5.0444 |  | 4.5444
1990-05-01 | 29.4167 | 28.2525 | 25.7807 | 24.5 | 25 | 25.5 | 26.2807 | 26.7807 | 3.636 |  | 4.9167 |  | 4.4167 |  | 3.9167 |  | 3.136 |  | 2.636
1990-05-02 | 26.35 | 28.4335 | 25.8314 | 24.5 | 25 | 25.5 | 26.3314 | 26.8314 | 0.51863 |  | 1.85 |  | 1.35 |  | 0.85 |  | 0.018628 |  | 0
1990-05-03 | 28.2167 | 28.4889 | 25.8469 | 24.5 | 25 | 25.5 | 26.3469 | 26.8469 | 2.3698 |  | 3.7167 |  | 3.2167 |  | 2.7167 |  | 1.8698 |  | 1.3698
1990-05-04 | 28.6167 | 28.5969 | 25.8771 | 24.5 | 25 | 25.5 | 26.3771 | 26.8771 | 2.7395 |  | 4.1167 |  | 3.6167 |  | 3.1167 |  | 2.2395 |  | 1.7395
1990-05-05 | 24.1708 | 28.6581 | 25.8943 | 24.5 | 25 | 25.5 | 26.3943 | 26.8943 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-05-06 | 26.4958 | 28.5806 | 25.8726 | 24.5 | 25 | 25.5 | 26.3726 | 26.8726 | 0.62328 |  | 1.9958 |  | 1.4958 |  | 0.99583 |  | 0.12328 |  | 0
1990-05-07 | 27.85 | 28.5633 | 25.8677 | 24.5 | 25 | 25.5 | 26.3677 | 26.8677 | 1.9823 |  | 3.35 |  | 2.85 |  | 2.35 |  | 1.4823 |  | 0.98227
1990-05-08 | 30.275 | 28.6507 | 25.8922 | 24.5 | 25 | 25.5 | 26.3922 | 26.8922 | 4.3828 |  | 5.775 |  | 5.275 |  | 4.775 |  | 3.8828 |  | 3.3828
1990-05-09 | 31.7417 | 28.7747 | 25.9269 | 24.5 | 25 | 25.5 | 26.4269 | 26.9269 | 5.8147 |  | 7.2417 |  | 6.7417 |  | 6.2417 |  | 5.3147 |  | 4.8147
1990-05-10 | 33.1458 | 28.9083 | 25.9643 | 24.5 | 25 | 25.5 | 26.4643 | 26.9643 | 7.1815 |  | 8.6458 |  | 8.1458 |  | 7.6458 |  | 6.6815 |  | 6.1815
1990-05-11 | 30.6458 | 29.1344 | 26.0276 | 24.5 | 25 | 25.5 | 26.5276 | 27.0276 | 4.6182 |  | 6.1458 |  | 5.6458 |  | 5.1458 |  | 4.1182 |  | 3.6182
1990-05-12 | 31.0667 | 29.2219 | 26.0521 | 24.5 | 25 | 25.5 | 26.5521 | 27.0521 | 5.0145 |  | 6.5667 |  | 6.0667 |  | 5.5667 |  | 4.5145 |  | 4.0145
1990-05-13 | 30.6375 | 29.3383 | 26.0847 | 24.5 | 25 | 25.5 | 26.5847 | 27.0847 | 4.5528 |  | 6.1375 |  | 5.6375 |  | 5.1375 |  | 4.0528 |  | 3.5528
1990-05-14 | 33.35 | 29.44 | 26.1132 | 24.5 | 25 | 25.5 | 26.6132 | 27.1132 | 7.2368 |  | 8.85 |  | 8.35 |  | 7.85 |  | 6.7368 |  | 6.2368
1990-05-15 | 33.8083 | 29.5974 | 26.1573 | 24.5 | 25 | 25.5 | 26.6573 | 27.1573 | 7.6511 |  | 9.3083 |  | 8.8083 |  | 8.3083 |  | 7.1511 |  | 6.6511
1990-05-16 | 32.6583 | 29.7906 | 26.2114 | 24.5 | 25 | 25.5 | 26.7114 | 27.2114 | 6.447 |  | 8.1583 |  | 7.6583 |  | 7.1583 |  | 5.947 |  | 5.447
1990-05-17 | 34.3583 | 29.9506 | 26.2562 | 24.5 | 25 | 25.5 | 26.7562 | 27.2562 | 8.1022 |  | 9.8583 |  | 9.3583 |  | 8.8583 |  | 7.6022 |  | 7.1022
1990-05-18 | 32.0375 | 30.1321 | 26.307 | 24.5 | 25 | 25.5 | 26.807 | 27.307 | 5.7305 |  | 7.5375 |  | 7.0375 |  | 6.5375 |  | 5.2305 |  | 4.7305
1990-05-19 | 32.0542 | 30.1882 | 26.3227 | 24.5 | 25 | 25.5 | 26.8227 | 27.3227 | 5.7315 |  | 7.5542 |  | 7.0542 |  | 6.5542 |  | 5.2315 |  | 4.7315
1990-05-20 | 32.5 | 30.2306 | 26.3346 | 24.5 | 25 | 25.5 | 26.8346 | 27.3346 | 6.1654 |  | 8 |  | 7.5 |  | 7 |  | 5.6654 |  | 5.1654
1990-05-21 | 33.3167 | 30.2561 | 26.3417 | 24.5 | 25 | 25.5 | 26.8417 | 27.3417 | 6.975 |  | 8.8167 |  | 8.3167 |  | 7.8167 |  | 6.475 |  | 5.975
1990-05-22 | 33.7625 | 30.3925 | 26.3799 | 24.5 | 25 | 25.5 | 26.8799 | 27.3799 | 7.3826 |  | 9.2625 |  | 8.7625 |  | 8.2625 |  | 6.8826 |  | 6.3826
1990-05-23 | 33.95 | 30.5521 | 26.4246 | 24.5 | 25 | 25.5 | 26.9246 | 27.4246 | 7.5254 |  | 9.45 |  | 8.95 |  | 8.45 |  | 7.0254 |  | 6.5254
1990-05-24 | 33.475 | 30.7875 | 26.4905 | 24.5 | 25 | 25.5 | 26.9905 | 27.4905 | 6.9845 |  | 8.975 |  | 8.475 |  | 7.975 |  | 6.4845 |  | 5.9845
1990-05-25 | 34.4708 | 30.9704 | 26.5417 | 24.5 | 25 | 25.5 | 27.0417 | 27.5417 | 7.9291 |  | 9.9708 |  | 9.4708 |  | 8.9708 |  | 7.4291 |  | 6.9291
1990-05-26 | 35.4667 | 31.1454 | 26.5907 | 24.5 | 25 | 25.5 | 27.0907 | 27.5907 | 8.876 |  | 10.9667 |  | 10.4667 |  | 9.9667 |  | 8.376 |  | 7.876
1990-05-27 | 36.1542 | 31.3231 | 26.6405 | 24.5 | 25 | 25.5 | 27.1405 | 27.6405 | 9.5137 |  | 11.6542 |  | 11.1542 |  | 10.6542 |  | 9.0137 |  | 8.5137
1990-05-28 | 36.6917 | 31.496 | 26.6889 | 24.5 | 25 | 25.5 | 27.1889 | 27.6889 | 10.0028 |  | 12.1917 |  | 11.6917 |  | 11.1917 |  | 9.5028 |  | 9.0028
1990-05-29 | 34.0042 | 31.6503 | 26.7321 | 24.5 | 25 | 25.5 | 27.2321 | 27.7321 | 7.2721 |  | 9.5042 |  | 9.0042 |  | 8.5042 |  | 6.7721 |  | 6.2721
1990-05-30 | 32.9292 | 31.7318 | 26.7549 | 24.5 | 25 | 25.5 | 27.2549 | 27.7549 | 6.1743 |  | 8.4292 |  | 7.9292 |  | 7.4292 |  | 5.6743 |  | 5.1743
1990-05-31 | 31.6875 | 31.7872 | 26.7704 | 24.5 | 25 | 25.5 | 27.2704 | 27.7704 | 4.9171 |  | 7.1875 |  | 6.6875 |  | 6.1875 |  | 4.4171 |  | 3.9171
1990-06-01 | 29.7083 | 31.8629 | 26.7916 | 24.5 | 25 | 25.5 | 27.2916 | 27.7916 | 2.9167 |  | 5.2083 |  | 4.7083 |  | 4.2083 |  | 2.4167 |  | 1.9167
1990-06-02 | 31.1333 | 31.9749 | 26.823 | 24.5 | 25 | 25.5 | 27.323 | 27.823 | 4.3104 |  | 6.6333 |  | 6.1333 |  | 5.6333 |  | 3.8104 |  | 3.3104
1990-06-03 | 32 | 32.0721 | 26.8502 | 24.5 | 25 | 25.5 | 27.3502 | 27.8502 | 5.1498 |  | 7.5 |  | 7 |  | 6.5 |  | 4.6498 |  | 4.1498
1990-06-04 | 32.3458 | 32.1849 | 26.8818 | 24.5 | 25 | 25.5 | 27.3818 | 27.8818 | 5.4641 |  | 7.8458 |  | 7.3458 |  | 6.8458 |  | 4.9641 |  | 4.4641
1990-06-05 | 31.3583 | 32.4574 | 26.9581 | 24.5 | 25 | 25.5 | 27.4581 | 27.9581 | 4.4003 |  | 6.8583 |  | 6.3583 |  | 5.8583 |  | 3.9003 |  | 3.4003
1990-06-06 | 32.4083 | 32.6194 | 27.0034 | 24.5 | 25 | 25.5 | 27.5034 | 28.0034 | 5.4049 |  | 7.9083 |  | 7.4083 |  | 6.9083 |  | 4.9049 |  | 4.4049
1990-06-07 | 34.5417 | 32.7714 | 27.046 | 24.5 | 25 | 25.5 | 27.546 | 28.046 | 7.4957 |  | 10.0417 |  | 9.5417 |  | 9.0417 |  | 6.9957 |  | 6.4957
1990-06-08 | 33.6542 | 32.9136 | 27.0858 | 24.5 | 25 | 25.5 | 27.5858 | 28.0858 | 6.5684 |  | 9.1542 |  | 8.6542 |  | 8.1542 |  | 6.0684 |  | 5.5684
1990-06-09 | 35.6042 | 32.9774 | 27.1037 | 24.5 | 25 | 25.5 | 27.6037 | 28.1037 | 8.5005 |  | 11.1042 |  | 10.6042 |  | 10.1042 |  | 8.0005 |  | 7.5005
1990-06-10 | 36.9458 | 33.0593 | 27.1266 | 24.5 | 25 | 25.5 | 27.6266 | 28.1266 | 9.8192 |  | 12.4458 |  | 11.9458 |  | 11.4458 |  | 9.3192 |  | 8.8192
1990-06-11 | 37.025 | 33.2693 | 27.1854 | 24.5 | 25 | 25.5 | 27.6854 | 28.1854 | 9.8396 |  | 12.525 |  | 12.025 |  | 11.525 |  | 9.3396 |  | 8.8396
1990-06-12 | 37.8917 | 33.4679 | 27.241 | 24.5 | 25 | 25.5 | 27.741 | 28.241 | 10.6507 |  | 13.3917 |  | 12.8917 |  | 12.3917 |  | 10.1507 |  | 9.6507
1990-06-13 | 37.3083 | 33.7097 | 27.3087 | 24.5 | 25 | 25.5 | 27.8087 | 28.3087 | 9.9996 |  | 12.8083 |  | 12.3083 |  | 11.8083 |  | 9.4996 |  | 8.9996
1990-06-14 | 34.7333 | 33.8417 | 27.3457 | 24.5 | 25 | 25.5 | 27.8457 | 28.3457 | 7.3877 |  | 10.2333 |  | 9.7333 |  | 9.2333 |  | 6.8877 |  | 6.3877
1990-06-15 | 35.725 | 33.8725 | 27.3543 | 24.5 | 25 | 25.5 | 27.8543 | 28.3543 | 8.3707 |  | 11.225 |  | 10.725 |  | 10.225 |  | 7.8707 |  | 7.3707
1990-06-16 | 35.6083 | 33.9747 | 27.3829 | 24.5 | 25 | 25.5 | 27.8829 | 28.3829 | 8.2254 |  | 11.1083 |  | 10.6083 |  | 10.1083 |  | 7.7254 |  | 7.2254
1990-06-17 | 35.1 | 34.0164 | 27.3946 | 24.5 | 25 | 25.5 | 27.8946 | 28.3946 | 7.7054 |  | 10.6 |  | 10.1 |  | 9.6 |  | 7.2054 |  | 6.7054
1990-06-18 | 36.8917 | 34.1185 | 27.4232 | 24.5 | 25 | 25.5 | 27.9232 | 28.4232 | 9.4685 |  | 12.3917 |  | 11.8917 |  | 11.3917 |  | 8.9685 |  | 8.4685
1990-06-19 | 35.8417 | 34.2797 | 27.4683 | 24.5 | 25 | 25.5 | 27.9683 | 28.4683 | 8.3733 |  | 11.3417 |  | 10.8417 |  | 10.3417 |  | 7.8733 |  | 7.3733
1990-06-20 | 33.5375 | 34.3911 | 27.4995 | 24.5 | 25 | 25.5 | 27.9995 | 28.4995 | 6.038 |  | 9.0375 |  | 8.5375 |  | 8.0375 |  | 5.538 |  | 5.038
1990-06-21 | 34.275 | 34.3985 | 27.5016 | 24.5 | 25 | 25.5 | 28.0016 | 28.5016 | 6.7734 |  | 9.775 |  | 9.275 |  | 8.775 |  | 6.2734 |  | 5.7734
1990-06-22 | 34.0792 | 34.4156 | 27.5064 | 24.5 | 25 | 25.5 | 28.0064 | 28.5064 | 6.5728 |  | 9.5792 |  | 9.0792 |  | 8.5792 |  | 6.0728 |  | 5.5728
1990-06-23 | 34.1542 | 34.4199 | 27.5076 | 24.5 | 25 | 25.5 | 28.0076 | 28.5076 | 6.6466 |  | 9.6542 |  | 9.1542 |  | 8.6542 |  | 6.1466 |  | 5.6466
1990-06-24 | 29.7833 | 34.4425 | 27.5139 | 24.5 | 25 | 25.5 | 28.0139 | 28.5139 | 2.2694 |  | 5.2833 |  | 4.7833 |  | 4.2833 |  | 1.7694 |  | 1.2694
1990-06-25 | 28.6833 | 34.2862 | 27.4702 | 24.5 | 25 | 25.5 | 27.9702 | 28.4702 | 1.2132 |  | 4.1833 |  | 3.6833 |  | 3.1833 |  | 0.71318 |  | 0.21318
1990-06-26 | 29.9167 | 34.0601 | 27.4068 | 24.5 | 25 | 25.5 | 27.9068 | 28.4068 | 2.5098 |  | 5.4167 |  | 4.9167 |  | 4.4167 |  | 2.0098 |  | 1.5098
1990-06-27 | 29.3458 | 33.8522 | 27.3486 | 24.5 | 25 | 25.5 | 27.8486 | 28.3486 | 1.9972 |  | 4.8458 |  | 4.3458 |  | 3.8458 |  | 1.4972 |  | 0.99721
1990-06-28 | 28.5875 | 33.6074 | 27.2801 | 24.5 | 25 | 25.5 | 27.7801 | 28.2801 | 1.3074 |  | 4.0875 |  | 3.5875 |  | 3.0875 |  | 0.80744 |  | 0.30744
1990-06-29 | 28.7375 | 33.4268 | 27.2295 | 24.5 | 25 | 25.5 | 27.7295 | 28.2295 | 1.508 |  | 4.2375 |  | 3.7375 |  | 3.2375 |  | 1.008 |  | 0.50799
1990-06-30 | 28.5542 | 33.2871 | 27.1904 | 24.5 | 25 | 25.5 | 27.6904 | 28.1904 | 1.3638 |  | 4.0542 |  | 3.5542 |  | 3.0542 |  | 0.86378 |  | 0.36378
1990-07-01 | 31.2333 | 33.1826 | 27.1611 | 24.5 | 25 | 25.5 | 27.6611 | 28.1611 | 4.0722 |  | 6.7333 |  | 6.2333 |  | 5.7333 |  | 3.5722 |  | 3.0722
1990-07-02 | 30.6708 | 33.2335 | 27.1754 | 24.5 | 25 | 25.5 | 27.6754 | 28.1754 | 3.4955 |  | 6.1708 |  | 5.6708 |  | 5.1708 |  | 2.9955 |  | 2.4955
1990-07-03 | 30.3375 | 33.2181 | 27.1711 | 24.5 | 25 | 25.5 | 27.6711 | 28.1711 | 3.1664 |  | 5.8375 |  | 5.3375 |  | 4.8375 |  | 2.6664 |  | 2.1664
1990-07-04 | 30.3917 | 33.1626 | 27.1555 | 24.5 | 25 | 25.5 | 27.6555 | 28.1555 | 3.2361 |  | 5.8917 |  | 5.3917 |  | 4.8917 |  | 2.7361 |  | 2.2361
1990-07-05 | 31.8833 | 33.0975 | 27.1373 | 24.5 | 25 | 25.5 | 27.6373 | 28.1373 | 4.746 |  | 7.3833 |  | 6.8833 |  | 6.3833 |  | 4.246 |  | 3.746
1990-07-06 | 32.8458 | 33.115 | 27.1422 | 24.5 | 25 | 25.5 | 27.6422 | 28.1422 | 5.7036 |  | 8.3458 |  | 7.8458 |  | 7.3458 |  | 5.2036 |  | 4.7036
1990-07-07 | 33.275 | 33.1296 | 27.1463 | 24.5 | 25 | 25.5 | 27.6463 | 28.1463 | 6.1287 |  | 8.775 |  | 8.275 |  | 7.775 |  | 5.6287 |  | 5.1287
1990-07-08 | 33.5708 | 33.0874 | 27.1345 | 24.5 | 25 | 25.5 | 27.6345 | 28.1345 | 6.4364 |  | 9.0708 |  | 8.5708 |  | 8.0708 |  | 5.9364 |  | 5.4364
1990-07-09 | 31.9208 | 33.0846 | 27.1337 | 24.5 | 25 | 25.5 | 27.6337 | 28.1337 | 4.7871 |  | 7.4208 |  | 6.9208 |  | 6.4208 |  | 4.2871 |  | 3.7871
1990-07-10 | 33.1833 | 32.9618 | 27.0993 | 24.5 | 25 | 25.5 | 27.5993 | 28.0993 | 6.084 |  | 8.6833 |  | 8.1833 |  | 7.6833 |  | 5.584 |  | 5.084
1990-07-11 | 35.4958 | 32.8364 | 27.0642 | 24.5 | 25 | 25.5 | 27.5642 | 28.0642 | 8.4316 |  | 10.9958 |  | 10.4958 |  | 9.9958 |  | 7.9316 |  | 7.4316
1990-07-12 | 32.2417 | 32.7854 | 27.0499 | 24.5 | 25 | 25.5 | 27.5499 | 28.0499 | 5.1918 |  | 7.7417 |  | 7.2417 |  | 6.7417 |  | 4.6918 |  | 4.1918
1990-07-13 | 29.2458 | 32.5971 | 26.9972 | 24.5 | 25 | 25.5 | 27.4972 | 27.9972 | 2.2486 |  | 4.7458 |  | 4.2458 |  | 3.7458 |  | 1.7486 |  | 1.2486
1990-07-14 | 28.0333 | 32.3283 | 26.9219 | 24.5 | 25 | 25.5 | 27.4219 | 27.9219 | 1.1114 |  | 3.5333 |  | 3.0333 |  | 2.5333 |  | 0.6114 |  | 0.1114
1990-07-15 | 29.0833 | 32.105 | 26.8594 | 24.5 | 25 | 25.5 | 27.3594 | 27.8594 | 2.2239 |  | 4.5833 |  | 4.0833 |  | 3.5833 |  | 1.7239 |  | 1.2239
1990-07-16 | 29.675 | 31.8836 | 26.7974 | 24.5 | 25 | 25.5 | 27.2974 | 27.7974 | 2.8776 |  | 5.175 |  | 4.675 |  | 4.175 |  | 2.3776 |  | 1.8776
1990-07-17 | 29.975 | 31.6858 | 26.742 | 24.5 | 25 | 25.5 | 27.242 | 27.742 | 3.233 |  | 5.475 |  | 4.975 |  | 4.475 |  | 2.733 |  | 2.233
1990-07-18 | 32.1167 | 31.515 | 26.6942 | 24.5 | 25 | 25.5 | 27.1942 | 27.6942 | 5.4225 |  | 7.6167 |  | 7.1167 |  | 6.6167 |  | 4.9225 |  | 4.4225
1990-07-19 | 34.6583 | 31.3558 | 26.6496 | 24.5 | 25 | 25.5 | 27.1496 | 27.6496 | 8.0087 |  | 10.1583 |  | 9.6583 |  | 9.1583 |  | 7.5087 |  | 7.0087
1990-07-20 | 31.9208 | 31.3164 | 26.6386 | 24.5 | 25 | 25.5 | 27.1386 | 27.6386 | 5.2822 |  | 7.4208 |  | 6.9208 |  | 6.4208 |  | 4.7822 |  | 4.2822
1990-07-21 | 30.7375 | 31.2625 | 26.6235 | 24.5 | 25 | 25.5 | 27.1235 | 27.6235 | 4.114 |  | 6.2375 |  | 5.7375 |  | 5.2375 |  | 3.614 |  | 3.114
1990-07-22 | 31.6917 | 31.1446 | 26.5905 | 24.5 | 25 | 25.5 | 27.0905 | 27.5905 | 5.1012 |  | 7.1917 |  | 6.6917 |  | 6.1917 |  | 4.6012 |  | 4.1012
1990-07-23 | 33.05 | 31.065 | 26.5682 | 24.5 | 25 | 25.5 | 27.0682 | 27.5682 | 6.4818 |  | 8.55 |  | 8.05 |  | 7.55 |  | 5.9818 |  | 5.4818
1990-07-24 | 32.6792 | 31.0282 | 26.5579 | 24.5 | 25 | 25.5 | 27.0579 | 27.5579 | 6.1213 |  | 8.1792 |  | 7.6792 |  | 7.1792 |  | 5.6213 |  | 5.1213
1990-07-25 | 31.775 | 31.1247 | 26.5849 | 24.5 | 25 | 25.5 | 27.0849 | 27.5849 | 5.1901 |  | 7.275 |  | 6.775 |  | 6.275 |  | 4.6901 |  | 4.1901
1990-07-26 | 32.775 | 31.2278 | 26.6138 | 24.5 | 25 | 25.5 | 27.1138 | 27.6138 | 6.1612 |  | 8.275 |  | 7.775 |  | 7.275 |  | 5.6612 |  | 5.1612
1990-07-27 | 31.2625 | 31.3231 | 26.6405 | 24.5 | 25 | 25.5 | 27.1405 | 27.6405 | 4.622 |  | 6.7625 |  | 6.2625 |  | 5.7625 |  | 4.122 |  | 3.622
1990-07-28 | 31.1 | 31.3869 | 26.6583 | 24.5 | 25 | 25.5 | 27.1583 | 27.6583 | 4.4417 |  | 6.6 |  | 6.1 |  | 5.6 |  | 3.9417 |  | 3.4417
1990-07-29 | 26.9042 | 31.4707 | 26.6818 | 24.5 | 25 | 25.5 | 27.1818 | 27.6818 | 0.22237 |  | 2.4042 |  | 1.9042 |  | 1.4042 |  | 0 |  | 0
1990-07-30 | 27.7958 | 31.4096 | 26.6647 | 24.5 | 25 | 25.5 | 27.1647 | 27.6647 | 1.1311 |  | 3.2958 |  | 2.7958 |  | 2.2958 |  | 0.63115 |  | 0.13115
1990-07-31 | 28.5917 | 31.3843 | 26.6576 | 24.5 | 25 | 25.5 | 27.1576 | 27.6576 | 1.9341 |  | 4.0917 |  | 3.5917 |  | 3.0917 |  | 1.4341 |  | 0.93406
1990-08-01 | 30.0292 | 31.2962 | 26.633 | 24.5 | 25 | 25.5 | 27.133 | 27.633 | 3.3962 |  | 5.5292 |  | 5.0292 |  | 4.5292 |  | 2.8962 |  | 2.3962
1990-08-02 | 29.025 | 31.2749 | 26.627 | 24.5 | 25 | 25.5 | 27.127 | 27.627 | 2.398 |  | 4.525 |  | 4.025 |  | 3.525 |  | 1.898 |  | 1.398
1990-08-03 | 31.6792 | 31.2311 | 26.6147 | 24.5 | 25 | 25.5 | 27.1147 | 27.6147 | 5.0645 |  | 7.1792 |  | 6.6792 |  | 6.1792 |  | 4.5645 |  | 4.0645
1990-08-04 | 32.0417 | 31.274 | 26.6267 | 24.5 | 25 | 25.5 | 27.1267 | 27.6267 | 5.4149 |  | 7.5417 |  | 7.0417 |  | 6.5417 |  | 4.9149 |  | 4.4149
1990-08-05 | 31.9792 | 31.2793 | 26.6282 | 24.5 | 25 | 25.5 | 27.1282 | 27.6282 | 5.351 |  | 7.4792 |  | 6.9792 |  | 6.4792 |  | 4.851 |  | 4.351
1990-08-06 | 32.4875 | 31.2504 | 26.6201 | 24.5 | 25 | 25.5 | 27.1201 | 27.6201 | 5.8674 |  | 7.9875 |  | 7.4875 |  | 6.9875 |  | 5.3674 |  | 4.8674
1990-08-07 | 32.4625 | 31.2242 | 26.6128 | 24.5 | 25 | 25.5 | 27.1128 | 27.6128 | 5.8497 |  | 7.9625 |  | 7.4625 |  | 6.9625 |  | 5.3497 |  | 4.8497
1990-08-08 | 31.4 | 31.1872 | 26.6024 | 24.5 | 25 | 25.5 | 27.1024 | 27.6024 | 4.7976 |  | 6.9 |  | 6.4 |  | 5.9 |  | 4.2976 |  | 3.7976
1990-08-09 | 31.3917 | 31.1699 | 26.5976 | 24.5 | 25 | 25.5 | 27.0976 | 27.5976 | 4.7941 |  | 6.8917 |  | 6.3917 |  | 5.8917 |  | 4.2941 |  | 3.7941
1990-08-10 | 30.5083 | 31.1101 | 26.5808 | 24.5 | 25 | 25.5 | 27.0808 | 27.5808 | 3.9275 |  | 6.0083 |  | 5.5083 |  | 5.0083 |  | 3.4275 |  | 2.9275
1990-08-11 | 30.95 | 30.9439 | 26.5343 | 24.5 | 25 | 25.5 | 27.0343 | 27.5343 | 4.4157 |  | 6.45 |  | 5.95 |  | 5.45 |  | 3.9157 |  | 3.4157
1990-08-12 | 30.9125 | 30.9008 | 26.5222 | 24.5 | 25 | 25.5 | 27.0222 | 27.5222 | 4.3903 |  | 6.4125 |  | 5.9125 |  | 5.4125 |  | 3.8903 |  | 3.3903
1990-08-13 | 29.8625 | 30.9564 | 26.5378 | 24.5 | 25 | 25.5 | 27.0378 | 27.5378 | 3.3247 |  | 5.3625 |  | 4.8625 |  | 4.3625 |  | 2.8247 |  | 2.3247
1990-08-14 | 31.4417 | 31.0174 | 26.5549 | 24.5 | 25 | 25.5 | 27.0549 | 27.5549 | 4.8868 |  | 6.9417 |  | 6.4417 |  | 5.9417 |  | 4.3868 |  | 3.8868
1990-08-15 | 30.1417 | 31.096 | 26.5769 | 24.5 | 25 | 25.5 | 27.0769 | 27.5769 | 3.5648 |  | 5.6417 |  | 5.1417 |  | 4.6417 |  | 3.0648 |  | 2.5648
1990-08-16 | 30.7083 | 31.1115 | 26.5812 | 24.5 | 25 | 25.5 | 27.0812 | 27.5812 | 4.1271 |  | 6.2083 |  | 5.7083 |  | 5.2083 |  | 3.6271 |  | 3.1271
1990-08-17 | 29.6167 | 31.136 | 26.5881 | 24.5 | 25 | 25.5 | 27.0881 | 27.5881 | 3.0286 |  | 5.1167 |  | 4.6167 |  | 4.1167 |  | 2.5286 |  | 2.0286
1990-08-18 | 29.2042 | 31.0526 | 26.5647 | 24.5 | 25 | 25.5 | 27.0647 | 27.5647 | 2.6394 |  | 4.7042 |  | 4.2042 |  | 3.7042 |  | 2.1394 |  | 1.6394
1990-08-19 | 31.0458 | 30.8708 | 26.5138 | 24.5 | 25 | 25.5 | 27.0138 | 27.5138 | 4.532 |  | 6.5458 |  | 6.0458 |  | 5.5458 |  | 4.032 |  | 3.532
1990-08-20 | 31.8 | 30.8417 | 26.5057 | 24.5 | 25 | 25.5 | 27.0057 | 27.5057 | 5.2943 |  | 7.3 |  | 6.8 |  | 6.3 |  | 4.7943 |  | 4.2943
1990-08-21 | 30.1542 | 30.8771 | 26.5156 | 24.5 | 25 | 25.5 | 27.0156 | 27.5156 | 3.6386 |  | 5.6542 |  | 5.1542 |  | 4.6542 |  | 3.1386 |  | 2.6386
1990-08-22 | 27.95 | 30.8258 | 26.5012 | 24.5 | 25 | 25.5 | 27.0012 | 27.5012 | 1.4488 |  | 3.45 |  | 2.95 |  | 2.45 |  | 0.94877 |  | 0.44877
1990-08-23 | 28.5917 | 30.6558 | 26.4536 | 24.5 | 25 | 25.5 | 26.9536 | 27.4536 | 2.138 |  | 4.0917 |  | 3.5917 |  | 3.0917 |  | 1.638 |  | 1.138
1990-08-24 | 27.1208 | 30.5196 | 26.4155 | 24.5 | 25 | 25.5 | 26.9155 | 27.4155 | 0.70535 |  | 2.6208 |  | 2.1208 |  | 1.6208 |  | 0.20535 |  | 0
1990-08-25 | 28.725 | 30.3644 | 26.372 | 24.5 | 25 | 25.5 | 26.872 | 27.372 | 2.353 |  | 4.225 |  | 3.725 |  | 3.225 |  | 1.853 |  | 1.353
1990-08-26 | 27.9875 | 30.2294 | 26.3342 | 24.5 | 25 | 25.5 | 26.8342 | 27.3342 | 1.6533 |  | 3.4875 |  | 2.9875 |  | 2.4875 |  | 1.1533 |  | 0.65326
1990-08-27 | 25.9667 | 30.1203 | 26.3037 | 24.5 | 25 | 25.5 | 26.8037 | 27.3037 | 0 |  | 1.4667 |  | 0.96667 |  | 0.46667 |  | 0 |  | 0
1990-08-28 | 27.3125 | 29.9492 | 26.2558 | 24.5 | 25 | 25.5 | 26.7558 | 27.2558 | 1.0567 |  | 2.8125 |  | 2.3125 |  | 1.8125 |  | 0.55673 |  | 0.056733
1990-08-29 | 28.4667 | 29.9628 | 26.2596 | 24.5 | 25 | 25.5 | 26.7596 | 27.2596 | 2.2071 |  | 3.9667 |  | 3.4667 |  | 2.9667 |  | 1.7071 |  | 1.2071
1990-08-30 | 29.1833 | 29.9851 | 26.2658 | 24.5 | 25 | 25.5 | 26.7658 | 27.2658 | 2.9175 |  | 4.6833 |  | 4.1833 |  | 3.6833 |  | 2.4175 |  | 1.9175
1990-08-31 | 29.2 | 30.0049 | 26.2714 | 24.5 | 25 | 25.5 | 26.7714 | 27.2714 | 2.9286 |  | 4.7 |  | 4.2 |  | 3.7 |  | 2.4286 |  | 1.9286
1990-09-01 | 27.5417 | 29.9772 | 26.2636 | 24.5 | 25 | 25.5 | 26.7636 | 27.2636 | 1.278 |  | 3.0417 |  | 2.5417 |  | 2.0417 |  | 0.77804 |  | 0.27804
1990-09-02 | 28.3208 | 29.9278 | 26.2498 | 24.5 | 25 | 25.5 | 26.7498 | 27.2498 | 2.0711 |  | 3.8208 |  | 3.3208 |  | 2.8208 |  | 1.5711 |  | 1.0711
1990-09-03 | 28.8917 | 29.8158 | 26.2184 | 24.5 | 25 | 25.5 | 26.7184 | 27.2184 | 2.6732 |  | 4.3917 |  | 3.8917 |  | 3.3917 |  | 2.1732 |  | 1.6732
1990-09-04 | 30.1417 | 29.7108 | 26.189 | 24.5 | 25 | 25.5 | 26.689 | 27.189 | 3.9526 |  | 5.6417 |  | 5.1417 |  | 4.6417 |  | 3.4526 |  | 2.9526
1990-09-05 | 28.3792 | 29.6496 | 26.1719 | 24.5 | 25 | 25.5 | 26.6719 | 27.1719 | 2.2073 |  | 3.8792 |  | 3.3792 |  | 2.8792 |  | 1.7073 |  | 1.2073
1990-09-06 | 28.5667 | 29.5126 | 26.1335 | 24.5 | 25 | 25.5 | 26.6335 | 27.1335 | 2.4331 |  | 4.0667 |  | 3.5667 |  | 3.0667 |  | 1.9331 |  | 1.4331
1990-09-07 | 29.4625 | 29.3828 | 26.0972 | 24.5 | 25 | 25.5 | 26.5972 | 27.0972 | 3.3653 |  | 4.9625 |  | 4.4625 |  | 3.9625 |  | 2.8653 |  | 2.3653
1990-09-08 | 29.9167 | 29.3182 | 26.0791 | 24.5 | 25 | 25.5 | 26.5791 | 27.0791 | 3.8376 |  | 5.4167 |  | 4.9167 |  | 4.4167 |  | 3.3376 |  | 2.8376
1990-09-09 | 29.975 | 29.269 | 26.0653 | 24.5 | 25 | 25.5 | 26.5653 | 27.0653 | 3.9097 |  | 5.475 |  | 4.975 |  | 4.475 |  | 3.4097 |  | 2.9097
1990-09-10 | 29.4667 | 29.2513 | 26.0604 | 24.5 | 25 | 25.5 | 26.5604 | 27.0604 | 3.4063 |  | 4.9667 |  | 4.4667 |  | 3.9667 |  | 2.9063 |  | 2.4063
1990-09-11 | 29.8625 | 29.2018 | 26.0465 | 24.5 | 25 | 25.5 | 26.5465 | 27.0465 | 3.816 |  | 5.3625 |  | 4.8625 |  | 4.3625 |  | 3.316 |  | 2.816
1990-09-12 | 30.0667 | 29.1668 | 26.0367 | 24.5 | 25 | 25.5 | 26.5367 | 27.0367 | 4.03 |  | 5.5667 |  | 5.0667 |  | 4.5667 |  | 3.53 |  | 3.03
1990-09-13 | 30.7792 | 29.1736 | 26.0386 | 24.5 | 25 | 25.5 | 26.5386 | 27.0386 | 4.7406 |  | 6.2792 |  | 5.7792 |  | 5.2792 |  | 4.2406 |  | 3.7406
1990-09-14 | 28.3833 | 29.1515 | 26.0324 | 24.5 | 25 | 25.5 | 26.5324 | 27.0324 | 2.3509 |  | 3.8833 |  | 3.3833 |  | 2.8833 |  | 1.8509 |  | 1.3509
1990-09-15 | 28.3167 | 29.0929 | 26.016 | 24.5 | 25 | 25.5 | 26.516 | 27.016 | 2.3007 |  | 3.8167 |  | 3.3167 |  | 2.8167 |  | 1.8007 |  | 1.3007
1990-09-16 | 29.975 | 29.0132 | 25.9937 | 24.5 | 25 | 25.5 | 26.4937 | 26.9937 | 3.9813 |  | 5.475 |  | 4.975 |  | 4.475 |  | 3.4813 |  | 2.9813
1990-09-17 | 30.1417 | 29.0251 | 25.997 | 24.5 | 25 | 25.5 | 26.497 | 26.997 | 4.1446 |  | 5.6417 |  | 5.1417 |  | 4.6417 |  | 3.6446 |  | 3.1446
1990-09-18 | 30.0208 | 29.0564 | 26.0058 | 24.5 | 25 | 25.5 | 26.5058 | 27.0058 | 4.015 |  | 5.5208 |  | 5.0208 |  | 4.5208 |  | 3.515 |  | 3.015
1990-09-19 | 29.7875 | 29.0222 | 25.9962 | 24.5 | 25 | 25.5 | 26.4962 | 26.9962 | 3.7913 |  | 5.2875 |  | 4.7875 |  | 4.2875 |  | 3.2913 |  | 2.7913
1990-09-20 | 29.3625 | 28.9551 | 25.9774 | 24.5 | 25 | 25.5 | 26.4774 | 26.9774 | 3.3851 |  | 4.8625 |  | 4.3625 |  | 3.8625 |  | 2.8851 |  | 2.3851
1990-09-21 | 29.5833 | 28.9288 | 25.9701 | 24.5 | 25 | 25.5 | 26.4701 | 26.9701 | 3.6133 |  | 5.0833 |  | 4.5833 |  | 4.0833 |  | 3.1133 |  | 2.6133
1990-09-22 | 29.4333 | 28.9832 | 25.9853 | 24.5 | 25 | 25.5 | 26.4853 | 26.9853 | 3.448 |  | 4.9333 |  | 4.4333 |  | 3.9333 |  | 2.948 |  | 2.448
1990-09-23 | 29.5042 | 29.0113 | 25.9932 | 24.5 | 25 | 25.5 | 26.4932 | 26.9932 | 3.511 |  | 5.0042 |  | 4.5042 |  | 4.0042 |  | 3.011 |  | 2.511
1990-09-24 | 29.6042 | 29.0907 | 26.0154 | 24.5 | 25 | 25.5 | 26.5154 | 27.0154 | 3.5888 |  | 5.1042 |  | 4.6042 |  | 4.1042 |  | 3.0888 |  | 2.5888
1990-09-25 | 29.5792 | 29.12 | 26.0236 | 24.5 | 25 | 25.5 | 26.5236 | 27.0236 | 3.5556 |  | 5.0792 |  | 4.5792 |  | 4.0792 |  | 3.0556 |  | 2.5556
1990-09-26 | 29.2083 | 29.1731 | 26.0385 | 24.5 | 25 | 25.5 | 26.5385 | 27.0385 | 3.1699 |  | 4.7083 |  | 4.2083 |  | 3.7083 |  | 2.6699 |  | 2.1699
1990-09-27 | 29.5083 | 29.2811 | 26.0687 | 24.5 | 25 | 25.5 | 26.5687 | 27.0687 | 3.4396 |  | 5.0083 |  | 4.5083 |  | 4.0083 |  | 2.9396 |  | 2.4396
1990-09-28 | 29.2583 | 29.3543 | 26.0892 | 24.5 | 25 | 25.5 | 26.5892 | 27.0892 | 3.1691 |  | 4.7583 |  | 4.2583 |  | 3.7583 |  | 2.6691 |  | 2.1691
1990-09-29 | 28.3208 | 29.3807 | 26.0966 | 24.5 | 25 | 25.5 | 26.5966 | 27.0966 | 2.2242 |  | 3.8208 |  | 3.3208 |  | 2.8208 |  | 1.7242 |  | 1.2242
1990-09-30 | 27.6542 | 29.3519 | 26.0885 | 24.5 | 25 | 25.5 | 26.5885 | 27.0885 | 1.5656 |  | 3.1542 |  | 2.6542 |  | 2.1542 |  | 1.0656 |  | 0.56562
1990-10-01 | 25.8708 | 29.3004 | 26.0741 | 24.5 | 25 | 25.5 | 26.5741 | 27.0741 | 0 |  | 1.3708 |  | 0.87083 |  | 0.37083 |  | 0 |  | 0
1990-10-02 | 26.7833 | 29.2447 | 26.0585 | 24.5 | 25 | 25.5 | 26.5585 | 27.0585 | 0.72481 |  | 2.2833 |  | 1.7833 |  | 1.2833 |  | 0.22481 |  | 0
1990-10-03 | 27.4542 | 29.1935 | 26.0442 | 24.5 | 25 | 25.5 | 26.5442 | 27.0442 | 1.41 |  | 2.9542 |  | 2.4542 |  | 1.9542 |  | 0.90999 |  | 0.40999
1990-10-04 | 28.0333 | 29.1456 | 26.0308 | 24.5 | 25 | 25.5 | 26.5308 | 27.0308 | 2.0026 |  | 3.5333 |  | 3.0333 |  | 2.5333 |  | 1.5026 |  | 1.0026
1990-10-05 | 27.6208 | 29.0753 | 26.0111 | 24.5 | 25 | 25.5 | 26.5111 | 27.0111 | 1.6098 |  | 3.1208 |  | 2.6208 |  | 2.1208 |  | 1.1098 |  | 0.60976
1990-10-06 | 27.8708 | 29.05 | 26.004 | 24.5 | 25 | 25.5 | 26.504 | 27.004 | 1.8668 |  | 3.3708 |  | 2.8708 |  | 2.3708 |  | 1.3668 |  | 0.86683
1990-10-07 | 28.3417 | 29.0268 | 25.9975 | 24.5 | 25 | 25.5 | 26.4975 | 26.9975 | 2.3442 |  | 3.8417 |  | 3.3417 |  | 2.8417 |  | 1.8442 |  | 1.3442
1990-10-08 | 27.7 | 28.9894 | 25.987 | 24.5 | 25 | 25.5 | 26.487 | 26.987 | 1.713 |  | 3.2 |  | 2.7 |  | 2.2 |  | 1.213 |  | 0.71296
1990-10-09 | 27.7417 | 28.9156 | 25.9664 | 24.5 | 25 | 25.5 | 26.4664 | 26.9664 | 1.7753 |  | 3.2417 |  | 2.7417 |  | 2.2417 |  | 1.2753 |  | 0.77531
1990-10-10 | 28.35 | 28.8411 | 25.9455 | 24.5 | 25 | 25.5 | 26.4455 | 26.9455 | 2.4045 |  | 3.85 |  | 3.35 |  | 2.85 |  | 1.9045 |  | 1.4045
1990-10-11 | 28.4083 | 28.8039 | 25.9351 | 24.5 | 25 | 25.5 | 26.4351 | 26.9351 | 2.4732 |  | 3.9083 |  | 3.4083 |  | 2.9083 |  | 1.9732 |  | 1.4732
1990-10-12 | 28.05 | 28.7554 | 25.9215 | 24.5 | 25 | 25.5 | 26.4215 | 26.9215 | 2.1285 |  | 3.55 |  | 3.05 |  | 2.55 |  | 1.6285 |  | 1.1285
1990-10-13 | 28.0208 | 28.6882 | 25.9027 | 24.5 | 25 | 25.5 | 26.4027 | 26.9027 | 2.1181 |  | 3.5208 |  | 3.0208 |  | 2.5208 |  | 1.6181 |  | 1.1181
1990-10-14 | 28.0208 | 28.5962 | 25.877 | 24.5 | 25 | 25.5 | 26.377 | 26.877 | 2.1439 |  | 3.5208 |  | 3.0208 |  | 2.5208 |  | 1.6439 |  | 1.1439
1990-10-15 | 27.225 | 28.5842 | 25.8736 | 24.5 | 25 | 25.5 | 26.3736 | 26.8736 | 1.3514 |  | 2.725 |  | 2.225 |  | 1.725 |  | 0.85143 |  | 0.35143
1990-10-16 | 24.8833 | 28.5478 | 25.8634 | 24.5 | 25 | 25.5 | 26.3634 | 26.8634 | 0 |  | 0.38333 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-17 | 23.975 | 28.3781 | 25.8159 | 24.5 | 25 | 25.5 | 26.3159 | 26.8159 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-18 | 24.2792 | 28.1725 | 25.7583 | 24.5 | 25 | 25.5 | 26.2583 | 26.7583 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-19 | 24.0875 | 27.9811 | 25.7047 | 24.5 | 25 | 25.5 | 26.2047 | 26.7047 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-20 | 23.6292 | 27.7911 | 25.6515 | 24.5 | 25 | 25.5 | 26.1515 | 26.6515 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-21 | 22.5333 | 27.6 | 25.598 | 24.5 | 25 | 25.5 | 26.098 | 26.598 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-22 | 22.7167 | 27.365 | 25.5322 | 24.5 | 25 | 25.5 | 26.0322 | 26.5322 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-23 | 21.9375 | 27.1411 | 25.4695 | 24.5 | 25 | 25.5 | 25.9695 | 26.4695 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-24 | 22.0167 | 26.8889 | 25.3989 | 24.5 | 25 | 25.5 | 25.8989 | 26.3989 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-25 | 21.7042 | 26.636 | 25.3281 | 24.5 | 25 | 25.5 | 25.8281 | 26.3281 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-26 | 22.475 | 26.3735 | 25.2546 | 24.5 | 25 | 25.5 | 25.7546 | 26.2546 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-27 | 22.6667 | 26.149 | 25.1917 | 24.5 | 25 | 25.5 | 25.6917 | 26.1917 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-28 | 23.475 | 25.921 | 25.1279 | 24.5 | 25 | 25.5 | 25.6279 | 26.1279 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-29 | 23.2167 | 25.7282 | 25.0739 | 24.5 | 25 | 25.5 | 25.5739 | 26.0739 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-30 | 23.525 | 25.5581 | 25.0263 | 24.5 | 25 | 25.5 | 25.5263 | 26.0263 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-31 | 23.2167 | 25.4204 | 24.9877 | 24.5 | 25 | 25.5 | 25.4877 | 25.9877 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-01 | 22.0625 | 25.3319 | 24.9629 | 24.5 | 25 | 25.5 | 25.4629 | 25.9629 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-02 | 22.5833 | 25.1746 | 24.9189 | 24.5 | 25 | 25.5 | 25.4189 | 25.9189 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-03 | 23.5958 | 25.0122 | 24.8734 | 24.5 | 25 | 25.5 | 25.3734 | 25.8734 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-04 | 23.3542 | 24.8643 | 24.832 | 24.5 | 25 | 25.5 | 25.332 | 25.832 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-05 | 22.3875 | 24.7221 | 24.7922 | 24.5 | 25 | 25.5 | 25.2922 | 25.7922 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-06 | 20.1292 | 24.5393 | 24.741 | 24.5 | 25 | 25.5 | 25.241 | 25.741 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-07 | 19.35 | 24.2656 | 24.6644 | 24.5 | 25 | 25.5 | 25.1644 | 25.6644 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-08 | 18.2708 | 23.9872 | 24.5864 | 24.5 | 25 | 25.5 | 25.0864 | 25.5864 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-09 | 18.4875 | 23.6715 | 24.498 | 24.5 | 25 | 25.5 | 24.998 | 25.498 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-10 | 19.4792 | 23.3428 | 24.406 | 24.5 | 25 | 25.5 | 24.906 | 25.406 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-11 | 20.1042 | 23.0451 | 24.3226 | 24.5 | 25 | 25.5 | 24.8226 | 25.3226 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-12 | 20.5875 | 22.7803 | 24.2485 | 24.5 | 25 | 25.5 | 24.7485 | 25.2485 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-13 | 20.425 | 22.5325 | 24.1791 | 24.5 | 25 | 25.5 | 24.6791 | 25.1791 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-14 | 20.4458 | 22.2793 | 24.1082 | 24.5 | 25 | 25.5 | 24.6082 | 25.1082 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-15 | 19.7583 | 22.0533 | 24.0449 | 24.5 | 25 | 25.5 | 24.5449 | 25.0449 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-16 | 19.4792 | 21.8825 | 23.9971 | 24.5 | 25 | 25.5 | 24.4971 | 24.9971 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-17 | 19.225 | 21.7326 | 23.9551 | 24.5 | 25 | 25.5 | 24.4551 | 24.9551 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-18 | 19.0333 | 21.5642 | 23.908 | 24.5 | 25 | 25.5 | 24.408 | 24.908 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-19 | 19.7625 | 21.3957 | 23.8608 | 24.5 | 25 | 25.5 | 24.3608 | 24.8608 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-20 | 19.25 | 21.2668 | 23.8247 | 24.5 | 25 | 25.5 | 24.3247 | 24.8247 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-21 | 19.3458 | 21.1574 | 23.7941 | 24.5 | 25 | 25.5 | 24.2941 | 24.7941 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-22 | 19.55 | 21.045 | 23.7626 | 24.5 | 25 | 25.5 | 24.2626 | 24.7626 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-23 | 20.45 | 20.9654 | 23.7403 | 24.5 | 25 | 25.5 | 24.2403 | 24.7403 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-24 | 17.3542 | 20.9132 | 23.7257 | 24.5 | 25 | 25.5 | 24.2257 | 24.7257 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-25 | 18.2333 | 20.7682 | 23.6851 | 24.5 | 25 | 25.5 | 24.1851 | 24.6851 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-26 | 17.4042 | 20.6268 | 23.6455 | 24.5 | 25 | 25.5 | 24.1455 | 24.6455 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-27 | 16.5875 | 20.4514 | 23.5964 | 24.5 | 25 | 25.5 | 24.0964 | 24.5964 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-28 | 16.6125 | 20.2218 | 23.5321 | 24.5 | 25 | 25.5 | 24.0321 | 24.5321 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-29 | 16.2833 | 20.0017 | 23.4705 | 24.5 | 25 | 25.5 | 23.9705 | 24.4705 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-30 | 15.4083 | 19.7603 | 23.4029 | 24.5 | 25 | 25.5 | 23.9029 | 24.4029 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-01 | 16.3792 | 19.5 | 23.33 | 24.5 | 25 | 25.5 | 23.83 | 24.33 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-02 | 16.4167 | 19.3106 | 23.277 | 24.5 | 25 | 25.5 | 23.777 | 24.277 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-03 | 16.4625 | 19.105 | 23.2194 | 24.5 | 25 | 25.5 | 23.7194 | 24.2194 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-04 | 15.9708 | 18.8672 | 23.1528 | 24.5 | 25 | 25.5 | 23.6528 | 24.1528 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-05 | 15.9083 | 18.6211 | 23.0839 | 24.5 | 25 | 25.5 | 23.5839 | 24.0839 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-06 | 15.9208 | 18.4051 | 23.0234 | 24.5 | 25 | 25.5 | 23.5234 | 24.0234 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-07 | 15.6708 | 18.2649 | 22.9842 | 24.5 | 25 | 25.5 | 23.4842 | 23.9842 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-08 | 15.5458 | 18.1422 | 22.9498 | 24.5 | 25 | 25.5 | 23.4498 | 23.9498 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-09 | 14.2375 | 18.0514 | 22.9244 | 24.5 | 25 | 25.5 | 23.4244 | 23.9244 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-10 | 13.1875 | 17.9097 | 22.8847 | 24.5 | 25 | 25.5 | 23.3847 | 23.8847 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-11 | 12.9958 | 17.7 | 22.826 | 24.5 | 25 | 25.5 | 23.326 | 23.826 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-12 | 13.5792 | 17.4631 | 22.7597 | 24.5 | 25 | 25.5 | 23.2597 | 23.7597 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-13 | 14.0417 | 17.2294 | 22.6942 | 24.5 | 25 | 25.5 | 23.1942 | 23.6942 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-14 | 14.7417 | 17.0167 | 22.6347 | 24.5 | 25 | 25.5 | 23.1347 | 23.6347 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-15 | 14.2208 | 16.8265 | 22.5814 | 24.5 | 25 | 25.5 | 23.0814 | 23.5814 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-16 | 16.2625 | 16.6419 | 22.5297 | 24.5 | 25 | 25.5 | 23.0297 | 23.5297 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-17 | 15.7958 | 16.5347 | 22.4997 | 24.5 | 25 | 25.5 | 22.9997 | 23.4997 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-18 | 15.8625 | 16.4204 | 22.4677 | 24.5 | 25 | 25.5 | 22.9677 | 23.4677 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-19 | 16.0167 | 16.3147 | 22.4381 | 24.5 | 25 | 25.5 | 22.9381 | 23.4381 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-20 | 15.5958 | 16.1899 | 22.4032 | 24.5 | 25 | 25.5 | 22.9032 | 23.4032 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-21 | 15.9458 | 16.0681 | 22.3691 | 24.5 | 25 | 25.5 | 22.8691 | 23.3691 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-22 | 16.1583 | 15.9547 | 22.3373 | 24.5 | 25 | 25.5 | 22.8373 | 23.3373 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-23 | 15.5417 | 15.8417 | 22.3057 | 24.5 | 25 | 25.5 | 22.8057 | 23.3057 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-24 | 15.8833 | 15.6781 | 22.2599 | 24.5 | 25 | 25.5 | 22.7599 | 23.2599 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-25 | 14.9583 | 15.629 | 22.2461 | 24.5 | 25 | 25.5 | 22.7461 | 23.2461 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-26 | 12.8917 | 15.5199 | 22.2156 | 24.5 | 25 | 25.5 | 22.7156 | 23.2156 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-27 | 12.5083 | 15.3694 | 22.1734 | 24.5 | 25 | 25.5 | 22.6734 | 23.1734 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-28 | 12.0625 | 15.2335 | 22.1354 | 24.5 | 25 | 25.5 | 22.6354 | 23.1354 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-29 | 12.4042 | 15.0818 | 22.0929 | 24.5 | 25 | 25.5 | 22.5929 | 23.0929 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-30 | 12.2583 | 14.9525 | 22.0567 | 24.5 | 25 | 25.5 | 22.5567 | 23.0567 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-31 | 12.0833 | 14.8475 | 22.0273 | 24.5 | 25 | 25.5 | 22.5273 | 23.0273 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## Hyderabad
Date | Daywise mean temperature | Running mean temperature (RMT) | Neutral temperature_IMAC | Baseline temperature calculated from PMV model | Plant adjusted I (Baseline + 0.5°C) | Plant adjusted II (Baseline + 1°C) | Plant adjusted I+ IMAC | Plant adjusted II+ IMAC | ACDD based on IMAC neutral temperature | 688.0245 | ACDD based on baseline temperature i.e. 24.5 calculated from the PMV model | 988.3583 | ACDD based on 0.5°C adjustment on baseline temperature because of plant | 863.9292 | ACDD based on 1°C adjustment on baseline temperature because of plant | 749.8375 | ACDD based on IMAC neutral temperature considering 0.5°C plant effect | 577.1638 | ACDD based on IMAC neutral temperature considering 1°C plant effect | 479.1277
1990-01-01 | 20.8625 | 21.7621 | 23.9634 | 24.5 | 25 | 25.5 | 24.4634 | 24.9634 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-02 | 20.1875 | 21.7461 | 23.9589 | 24.5 | 25 | 25.5 | 24.4589 | 24.9589 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-03 | 20.4125 | 21.6956 | 23.9448 | 24.5 | 25 | 25.5 | 24.4448 | 24.9448 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-04 | 20.6333 | 21.5839 | 23.9135 | 24.5 | 25 | 25.5 | 24.4135 | 24.9135 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-05 | 20.7208 | 21.4579 | 23.8782 | 24.5 | 25 | 25.5 | 24.3782 | 24.8782 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-06 | 21.475 | 21.3537 | 23.849 | 24.5 | 25 | 25.5 | 24.349 | 24.849 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-07 | 21.6625 | 21.3017 | 23.8345 | 24.5 | 25 | 25.5 | 24.3345 | 24.8345 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-08 | 22.125 | 21.2979 | 23.8334 | 24.5 | 25 | 25.5 | 24.3334 | 24.8334 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-09 | 23.05 | 21.3157 | 23.8384 | 24.5 | 25 | 25.5 | 24.3384 | 24.8384 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-10 | 23.6833 | 21.3565 | 23.8498 | 24.5 | 25 | 25.5 | 24.3498 | 24.8498 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-11 | 23.3792 | 21.3718 | 23.8541 | 24.5 | 25 | 25.5 | 24.3541 | 24.8541 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-12 | 23.5083 | 21.3729 | 23.8544 | 24.5 | 25 | 25.5 | 24.3544 | 24.8544 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-13 | 22.7125 | 21.3479 | 23.8474 | 24.5 | 25 | 25.5 | 24.3474 | 24.8474 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-14 | 23.4708 | 21.3356 | 23.844 | 24.5 | 25 | 25.5 | 24.344 | 24.844 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-15 | 23.3958 | 21.3908 | 23.8594 | 24.5 | 25 | 25.5 | 24.3594 | 24.8594 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-16 | 22.7042 | 21.5001 | 23.89 | 24.5 | 25 | 25.5 | 24.39 | 24.89 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-17 | 23.6667 | 21.6047 | 23.9193 | 24.5 | 25 | 25.5 | 24.4193 | 24.9193 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-18 | 23.5292 | 21.7544 | 23.9612 | 24.5 | 25 | 25.5 | 24.4612 | 24.9612 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-19 | 23.7875 | 21.9262 | 24.0093 | 24.5 | 25 | 25.5 | 24.5093 | 25.0093 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-20 | 23.4042 | 22.1014 | 24.0584 | 24.5 | 25 | 25.5 | 24.5584 | 25.0584 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-21 | 24 | 22.2067 | 24.0879 | 24.5 | 25 | 25.5 | 24.5879 | 25.0879 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-22 | 23.8583 | 22.2886 | 24.1108 | 24.5 | 25 | 25.5 | 24.6108 | 25.1108 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-23 | 24.325 | 22.3175 | 24.1189 | 24.5 | 25 | 25.5 | 24.6189 | 25.1189 | 0.2061 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-24 | 23.6667 | 22.3497 | 24.1279 | 24.5 | 25 | 25.5 | 24.6279 | 25.1279 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-25 | 24.0917 | 22.3799 | 24.1364 | 24.5 | 25 | 25.5 | 24.6364 | 25.1364 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-26 | 23.3542 | 22.4336 | 24.1514 | 24.5 | 25 | 25.5 | 24.6514 | 25.1514 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-27 | 22.8208 | 22.5176 | 24.1749 | 24.5 | 25 | 25.5 | 24.6749 | 25.1749 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-28 | 22.3458 | 22.5965 | 24.197 | 24.5 | 25 | 25.5 | 24.697 | 25.197 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-29 | 23.5583 | 22.6376 | 24.2085 | 24.5 | 25 | 25.5 | 24.7085 | 25.2085 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-30 | 23.3542 | 22.719 | 24.2313 | 24.5 | 25 | 25.5 | 24.7313 | 25.2313 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-01-31 | 22.9 | 22.7915 | 24.2516 | 24.5 | 25 | 25.5 | 24.7516 | 25.2516 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-01 | 23.7375 | 22.8594 | 24.2706 | 24.5 | 25 | 25.5 | 24.7706 | 25.2706 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-02 | 24.0167 | 22.9778 | 24.3038 | 24.5 | 25 | 25.5 | 24.8038 | 25.3038 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-03 | 24.6833 | 23.0979 | 24.3374 | 24.5 | 25 | 25.5 | 24.8374 | 25.3374 | 0.34592 |  | 0.18333 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-04 | 24.4583 | 23.2329 | 24.3752 | 24.5 | 25 | 25.5 | 24.8752 | 25.3752 | 0.083117 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-05 | 24.8125 | 23.3575 | 24.4101 | 24.5 | 25 | 25.5 | 24.9101 | 25.4101 | 0.4024 |  | 0.3125 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-06 | 25.2125 | 23.4687 | 24.4413 | 24.5 | 25 | 25.5 | 24.9413 | 25.4413 | 0.77125 |  | 0.7125 |  | 0.2125 |  | 0 |  | 0.27125 |  | 0
1990-02-07 | 25.3833 | 23.5871 | 24.4744 | 24.5 | 25 | 25.5 | 24.9744 | 25.4744 | 0.90895 |  | 0.88333 |  | 0.38333 |  | 0 |  | 0.40895 |  | 0
1990-02-08 | 25.2917 | 23.6957 | 24.5048 | 24.5 | 25 | 25.5 | 25.0048 | 25.5048 | 0.78687 |  | 0.79167 |  | 0.29167 |  | 0 |  | 0.28687 |  | 0
1990-02-09 | 25.95 | 23.7704 | 24.5257 | 24.5 | 25 | 25.5 | 25.0257 | 25.5257 | 1.4243 |  | 1.45 |  | 0.95 |  | 0.45 |  | 0.92428 |  | 0.42428
1990-02-10 | 25.7167 | 23.846 | 24.5469 | 24.5 | 25 | 25.5 | 25.0469 | 25.5469 | 1.1698 |  | 1.2167 |  | 0.71667 |  | 0.21667 |  | 0.66979 |  | 0.16979
1990-02-11 | 25.9583 | 23.9239 | 24.5687 | 24.5 | 25 | 25.5 | 25.0687 | 25.5687 | 1.3896 |  | 1.4583 |  | 0.95833 |  | 0.45833 |  | 0.88964 |  | 0.38964
1990-02-12 | 25.5333 | 24.0056 | 24.5916 | 24.5 | 25 | 25.5 | 25.0916 | 25.5916 | 0.94178 |  | 1.0333 |  | 0.53333 |  | 0.033333 |  | 0.44178 |  | 0
1990-02-13 | 25.575 | 24.0996 | 24.6179 | 24.5 | 25 | 25.5 | 25.1179 | 25.6179 | 0.95712 |  | 1.075 |  | 0.575 |  | 0.075 |  | 0.45712 |  | 0
1990-02-14 | 26.0583 | 24.1697 | 24.6375 | 24.5 | 25 | 25.5 | 25.1375 | 25.6375 | 1.4208 |  | 1.5583 |  | 1.0583 |  | 0.55833 |  | 0.92081 |  | 0.42081
1990-02-15 | 25.3 | 24.2585 | 24.6624 | 24.5 | 25 | 25.5 | 25.1624 | 25.6624 | 0.63763 |  | 0.8 |  | 0.3 |  | 0 |  | 0.13763 |  | 0
1990-02-16 | 25.3542 | 24.345 | 24.6866 | 24.5 | 25 | 25.5 | 25.1866 | 25.6866 | 0.66757 |  | 0.85417 |  | 0.35417 |  | 0 |  | 0.16757 |  | 0
1990-02-17 | 25.9583 | 24.4012 | 24.7024 | 24.5 | 25 | 25.5 | 25.2024 | 25.7024 | 1.256 |  | 1.4583 |  | 0.95833 |  | 0.45833 |  | 0.75598 |  | 0.25598
1990-02-18 | 26.7375 | 24.4822 | 24.725 | 24.5 | 25 | 25.5 | 25.225 | 25.725 | 2.0125 |  | 2.2375 |  | 1.7375 |  | 1.2375 |  | 1.5125 |  | 1.0125
1990-02-19 | 23.5042 | 24.5806 | 24.7526 | 24.5 | 25 | 25.5 | 25.2526 | 25.7526 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-20 | 22.5458 | 24.5839 | 24.7535 | 24.5 | 25 | 25.5 | 25.2535 | 25.7535 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-21 | 24.0208 | 24.5354 | 24.7399 | 24.5 | 25 | 25.5 | 25.2399 | 25.7399 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-22 | 24.0042 | 24.5408 | 24.7414 | 24.5 | 25 | 25.5 | 25.2414 | 25.7414 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-23 | 24.8083 | 24.5301 | 24.7384 | 24.5 | 25 | 25.5 | 25.2384 | 25.7384 | 0.069894 |  | 0.30833 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-24 | 24.45 | 24.5682 | 24.7491 | 24.5 | 25 | 25.5 | 25.2491 | 25.7491 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-02-25 | 25.8625 | 24.5801 | 24.7524 | 24.5 | 25 | 25.5 | 25.2524 | 25.7524 | 1.1101 |  | 1.3625 |  | 0.8625 |  | 0.3625 |  | 0.61006 |  | 0.11006
1990-02-26 | 26.4625 | 24.6637 | 24.7758 | 24.5 | 25 | 25.5 | 25.2758 | 25.7758 | 1.6867 |  | 1.9625 |  | 1.4625 |  | 0.9625 |  | 1.1867 |  | 0.68665
1990-02-27 | 26.7542 | 24.7851 | 24.8098 | 24.5 | 25 | 25.5 | 25.3098 | 25.8098 | 1.9443 |  | 2.2542 |  | 1.7542 |  | 1.2542 |  | 1.4443 |  | 0.94433
1990-02-28 | 27.2292 | 24.9321 | 24.851 | 24.5 | 25 | 25.5 | 25.351 | 25.851 | 2.3782 |  | 2.7292 |  | 2.2292 |  | 1.7292 |  | 1.8782 |  | 1.3782
1990-03-01 | 26.9583 | 25.0544 | 24.8852 | 24.5 | 25 | 25.5 | 25.3852 | 25.8852 | 2.0731 |  | 2.4583 |  | 1.9583 |  | 1.4583 |  | 1.5731 |  | 1.0731
1990-03-02 | 27.0958 | 25.1746 | 24.9189 | 24.5 | 25 | 25.5 | 25.4189 | 25.9189 | 2.1769 |  | 2.5958 |  | 2.0958 |  | 1.5958 |  | 1.6769 |  | 1.1769
1990-03-03 | 27.1292 | 25.3144 | 24.958 | 24.5 | 25 | 25.5 | 25.458 | 25.958 | 2.1711 |  | 2.6292 |  | 2.1292 |  | 1.6292 |  | 1.6711 |  | 1.1711
1990-03-04 | 27.3708 | 25.4275 | 24.9897 | 24.5 | 25 | 25.5 | 25.4897 | 25.9897 | 2.3811 |  | 2.8708 |  | 2.3708 |  | 1.8708 |  | 1.8811 |  | 1.3811
1990-03-05 | 28.0042 | 25.5393 | 25.021 | 24.5 | 25 | 25.5 | 25.521 | 26.021 | 2.9832 |  | 3.5042 |  | 3.0042 |  | 2.5042 |  | 2.4832 |  | 1.9832
1990-03-06 | 28.7958 | 25.65 | 25.052 | 24.5 | 25 | 25.5 | 25.552 | 26.052 | 3.7438 |  | 4.2958 |  | 3.7958 |  | 3.2958 |  | 3.2438 |  | 2.7438
1990-03-07 | 28.1542 | 25.7946 | 25.0925 | 24.5 | 25 | 25.5 | 25.5925 | 26.0925 | 3.0617 |  | 3.6542 |  | 3.1542 |  | 2.6542 |  | 2.5617 |  | 2.0617
1990-03-08 | 27.875 | 25.906 | 25.1237 | 24.5 | 25 | 25.5 | 25.6237 | 26.1237 | 2.7513 |  | 3.375 |  | 2.875 |  | 2.375 |  | 2.2513 |  | 1.7513
1990-03-09 | 27.7042 | 25.9947 | 25.1485 | 24.5 | 25 | 25.5 | 25.6485 | 26.1485 | 2.5556 |  | 3.2042 |  | 2.7042 |  | 2.2042 |  | 2.0556 |  | 1.5556
1990-03-10 | 27.65 | 26.0721 | 25.1702 | 24.5 | 25 | 25.5 | 25.6702 | 26.1702 | 2.4798 |  | 3.15 |  | 2.65 |  | 2.15 |  | 1.9798 |  | 1.4798
1990-03-11 | 28.3292 | 26.1507 | 25.1922 | 24.5 | 25 | 25.5 | 25.6922 | 26.1922 | 3.137 |  | 3.8292 |  | 3.3292 |  | 2.8292 |  | 2.637 |  | 2.137
1990-03-12 | 29.3208 | 26.23 | 25.2144 | 24.5 | 25 | 25.5 | 25.7144 | 26.2144 | 4.1064 |  | 4.8208 |  | 4.3208 |  | 3.8208 |  | 3.6064 |  | 3.1064
1990-03-13 | 29.5583 | 26.3501 | 25.248 | 24.5 | 25 | 25.5 | 25.748 | 26.248 | 4.3103 |  | 5.0583 |  | 4.5583 |  | 4.0583 |  | 3.8103 |  | 3.3103
1990-03-14 | 30.0917 | 26.4701 | 25.2816 | 24.5 | 25 | 25.5 | 25.7816 | 26.2816 | 4.81 |  | 5.5917 |  | 5.0917 |  | 4.5917 |  | 4.31 |  | 3.81
1990-03-15 | 30.4833 | 26.6221 | 25.3242 | 24.5 | 25 | 25.5 | 25.8242 | 26.3242 | 5.1591 |  | 5.9833 |  | 5.4833 |  | 4.9833 |  | 4.6591 |  | 4.1591
1990-03-16 | 30.575 | 26.7857 | 25.37 | 24.5 | 25 | 25.5 | 25.87 | 26.37 | 5.205 |  | 6.075 |  | 5.575 |  | 5.075 |  | 4.705 |  | 4.205
1990-03-17 | 30.5125 | 26.9362 | 25.4122 | 24.5 | 25 | 25.5 | 25.9122 | 26.4122 | 5.1003 |  | 6.0125 |  | 5.5125 |  | 5.0125 |  | 4.6003 |  | 4.1003
1990-03-18 | 30.9708 | 27.11 | 25.4608 | 24.5 | 25 | 25.5 | 25.9608 | 26.4608 | 5.51 |  | 6.4708 |  | 5.9708 |  | 5.4708 |  | 5.01 |  | 4.51
1990-03-19 | 30.2833 | 27.2972 | 25.5132 | 24.5 | 25 | 25.5 | 26.0132 | 26.5132 | 4.7701 |  | 5.7833 |  | 5.2833 |  | 4.7833 |  | 4.2701 |  | 3.7701
1990-03-20 | 29.5167 | 27.4414 | 25.5536 | 24.5 | 25 | 25.5 | 26.0536 | 26.5536 | 3.9631 |  | 5.0167 |  | 4.5167 |  | 4.0167 |  | 3.4631 |  | 2.9631
1990-03-21 | 29.9833 | 27.534 | 25.5795 | 24.5 | 25 | 25.5 | 26.0795 | 26.5795 | 4.4038 |  | 5.4833 |  | 4.9833 |  | 4.4833 |  | 3.9038 |  | 3.4038
1990-03-22 | 30.15 | 27.75 | 25.64 | 24.5 | 25 | 25.5 | 26.14 | 26.64 | 4.51 |  | 5.65 |  | 5.15 |  | 4.65 |  | 4.01 |  | 3.51
1990-03-23 | 28.9125 | 28.0035 | 25.711 | 24.5 | 25 | 25.5 | 26.211 | 26.711 | 3.2015 |  | 4.4125 |  | 3.9125 |  | 3.4125 |  | 2.7015 |  | 2.2015
1990-03-24 | 29.625 | 28.1665 | 25.7566 | 24.5 | 25 | 25.5 | 26.2566 | 26.7566 | 3.8684 |  | 5.125 |  | 4.625 |  | 4.125 |  | 3.3684 |  | 2.8684
1990-03-25 | 28.1958 | 28.3539 | 25.8091 | 24.5 | 25 | 25.5 | 26.3091 | 26.8091 | 2.3867 |  | 3.6958 |  | 3.1958 |  | 2.6958 |  | 1.8867 |  | 1.3867
1990-03-26 | 30.4 | 28.4668 | 25.8407 | 24.5 | 25 | 25.5 | 26.3407 | 26.8407 | 4.5593 |  | 5.9 |  | 5.4 |  | 4.9 |  | 4.0593 |  | 3.5593
1990-03-27 | 29.5833 | 28.6651 | 25.8962 | 24.5 | 25 | 25.5 | 26.3962 | 26.8962 | 3.6871 |  | 5.0833 |  | 4.5833 |  | 4.0833 |  | 3.1871 |  | 2.6871
1990-03-28 | 30.2792 | 28.7892 | 25.931 | 24.5 | 25 | 25.5 | 26.431 | 26.931 | 4.3482 |  | 5.7792 |  | 5.2792 |  | 4.7792 |  | 3.8482 |  | 3.3482
1990-03-29 | 30.0458 | 28.9164 | 25.9666 | 24.5 | 25 | 25.5 | 26.4666 | 26.9666 | 4.0792 |  | 5.5458 |  | 5.0458 |  | 4.5458 |  | 3.5792 |  | 3.0792
1990-03-30 | 30.425 | 29.0261 | 25.9973 | 24.5 | 25 | 25.5 | 26.4973 | 26.9973 | 4.4277 |  | 5.925 |  | 5.425 |  | 4.925 |  | 3.9277 |  | 3.4277
1990-03-31 | 30.9083 | 29.1326 | 26.0271 | 24.5 | 25 | 25.5 | 26.5271 | 27.0271 | 4.8812 |  | 6.4083 |  | 5.9083 |  | 5.4083 |  | 4.3812 |  | 3.8812
1990-04-01 | 31.8375 | 29.2643 | 26.064 | 24.5 | 25 | 25.5 | 26.564 | 27.064 | 5.7735 |  | 7.3375 |  | 6.8375 |  | 6.3375 |  | 5.2735 |  | 4.7735
1990-04-02 | 31.4167 | 29.4224 | 26.1083 | 24.5 | 25 | 25.5 | 26.6083 | 27.1083 | 5.3084 |  | 6.9167 |  | 6.4167 |  | 5.9167 |  | 4.8084 |  | 4.3084
1990-04-03 | 30.5833 | 29.5653 | 26.1483 | 24.5 | 25 | 25.5 | 26.6483 | 27.1483 | 4.4351 |  | 6.0833 |  | 5.5833 |  | 5.0833 |  | 3.9351 |  | 3.4351
1990-04-04 | 31.3167 | 29.6724 | 26.1783 | 24.5 | 25 | 25.5 | 26.6783 | 27.1783 | 5.1384 |  | 6.8167 |  | 6.3167 |  | 5.8167 |  | 4.6384 |  | 4.1384
1990-04-05 | 30.6083 | 29.7828 | 26.2092 | 24.5 | 25 | 25.5 | 26.7092 | 27.2092 | 4.3992 |  | 6.1083 |  | 5.6083 |  | 5.1083 |  | 3.8992 |  | 3.3992
1990-04-06 | 31.5417 | 29.8432 | 26.2261 | 24.5 | 25 | 25.5 | 26.7261 | 27.2261 | 5.3156 |  | 7.0417 |  | 6.5417 |  | 6.0417 |  | 4.8156 |  | 4.3156
1990-04-07 | 31.0792 | 29.9561 | 26.2577 | 24.5 | 25 | 25.5 | 26.7577 | 27.2577 | 4.8215 |  | 6.5792 |  | 6.0792 |  | 5.5792 |  | 4.3215 |  | 3.8215
1990-04-08 | 31.9625 | 30.0629 | 26.2876 | 24.5 | 25 | 25.5 | 26.7876 | 27.2876 | 5.6749 |  | 7.4625 |  | 6.9625 |  | 6.4625 |  | 5.1749 |  | 4.6749
1990-04-09 | 33.0958 | 30.2049 | 26.3274 | 24.5 | 25 | 25.5 | 26.8274 | 27.3274 | 6.7685 |  | 8.5958 |  | 8.0958 |  | 7.5958 |  | 6.2685 |  | 5.7685
1990-04-10 | 33.1083 | 30.3864 | 26.3782 | 24.5 | 25 | 25.5 | 26.8782 | 27.3782 | 6.7301 |  | 8.6083 |  | 8.1083 |  | 7.6083 |  | 6.2301 |  | 5.7301
1990-04-11 | 33.2583 | 30.5457 | 26.4228 | 24.5 | 25 | 25.5 | 26.9228 | 27.4228 | 6.8355 |  | 8.7583 |  | 8.2583 |  | 7.7583 |  | 6.3355 |  | 5.8355
1990-04-12 | 33.0583 | 30.6769 | 26.4595 | 24.5 | 25 | 25.5 | 26.9595 | 27.4595 | 6.5988 |  | 8.5583 |  | 8.0583 |  | 7.5583 |  | 6.0988 |  | 5.5988
1990-04-13 | 33.825 | 30.7936 | 26.4922 | 24.5 | 25 | 25.5 | 26.9922 | 27.4922 | 7.3328 |  | 9.325 |  | 8.825 |  | 8.325 |  | 6.8328 |  | 6.3328
1990-04-14 | 33.5667 | 30.9181 | 26.5271 | 24.5 | 25 | 25.5 | 27.0271 | 27.5271 | 7.0396 |  | 9.0667 |  | 8.5667 |  | 8.0667 |  | 6.5396 |  | 6.0396
1990-04-15 | 34.05 | 31.0208 | 26.5558 | 24.5 | 25 | 25.5 | 27.0558 | 27.5558 | 7.4942 |  | 9.55 |  | 9.05 |  | 8.55 |  | 6.9942 |  | 6.4942
1990-04-16 | 34.1583 | 31.1367 | 26.5883 | 24.5 | 25 | 25.5 | 27.0883 | 27.5883 | 7.5701 |  | 9.6583 |  | 9.1583 |  | 8.6583 |  | 7.0701 |  | 6.5701
1990-04-17 | 31.9917 | 31.2582 | 26.6223 | 24.5 | 25 | 25.5 | 27.1223 | 27.6223 | 5.3694 |  | 7.4917 |  | 6.9917 |  | 6.4917 |  | 4.8694 |  | 4.3694
1990-04-18 | 33.7042 | 31.2922 | 26.6318 | 24.5 | 25 | 25.5 | 27.1318 | 27.6318 | 7.0723 |  | 9.2042 |  | 8.7042 |  | 8.2042 |  | 6.5723 |  | 6.0723
1990-04-19 | 32.6917 | 31.4062 | 26.6638 | 24.5 | 25 | 25.5 | 27.1638 | 27.6638 | 6.0279 |  | 8.1917 |  | 7.6917 |  | 7.1917 |  | 5.5279 |  | 5.0279
1990-04-20 | 29.0625 | 31.5121 | 26.6934 | 24.5 | 25 | 25.5 | 27.1934 | 27.6934 | 2.3691 |  | 4.5625 |  | 4.0625 |  | 3.5625 |  | 1.8691 |  | 1.3691
1990-04-21 | 30.475 | 31.4814 | 26.6848 | 24.5 | 25 | 25.5 | 27.1848 | 27.6848 | 3.7902 |  | 5.975 |  | 5.475 |  | 4.975 |  | 3.2902 |  | 2.7902
1990-04-22 | 30.25 | 31.4922 | 26.6878 | 24.5 | 25 | 25.5 | 27.1878 | 27.6878 | 3.5622 |  | 5.75 |  | 5.25 |  | 4.75 |  | 3.0622 |  | 2.5622
1990-04-23 | 31.9583 | 31.5368 | 26.7003 | 24.5 | 25 | 25.5 | 27.2003 | 27.7003 | 5.258 |  | 7.4583 |  | 6.9583 |  | 6.4583 |  | 4.758 |  | 4.258
1990-04-24 | 31.0625 | 31.6146 | 26.7221 | 24.5 | 25 | 25.5 | 27.2221 | 27.7221 | 4.3404 |  | 6.5625 |  | 6.0625 |  | 5.5625 |  | 3.8404 |  | 3.3404
1990-04-25 | 29.5 | 31.7101 | 26.7488 | 24.5 | 25 | 25.5 | 27.2488 | 27.7488 | 2.7512 |  | 5 |  | 4.5 |  | 4 |  | 2.2512 |  | 1.7512
1990-04-26 | 28.5042 | 31.6801 | 26.7404 | 24.5 | 25 | 25.5 | 27.2404 | 27.7404 | 1.7637 |  | 4.0042 |  | 3.5042 |  | 3.0042 |  | 1.2637 |  | 0.76373
1990-04-27 | 30.0875 | 31.6442 | 26.7304 | 24.5 | 25 | 25.5 | 27.2304 | 27.7304 | 3.3571 |  | 5.5875 |  | 5.0875 |  | 4.5875 |  | 2.8571 |  | 2.3571
1990-04-28 | 30.1917 | 31.6378 | 26.7286 | 24.5 | 25 | 25.5 | 27.2286 | 27.7286 | 3.4631 |  | 5.6917 |  | 5.1917 |  | 4.6917 |  | 2.9631 |  | 2.4631
1990-04-29 | 31.0125 | 31.6426 | 26.7299 | 24.5 | 25 | 25.5 | 27.2299 | 27.7299 | 4.2826 |  | 6.5125 |  | 6.0125 |  | 5.5125 |  | 3.7826 |  | 3.2826
1990-04-30 | 32.2083 | 31.6622 | 26.7354 | 24.5 | 25 | 25.5 | 27.2354 | 27.7354 | 5.4729 |  | 7.7083 |  | 7.2083 |  | 6.7083 |  | 4.9729 |  | 4.4729
1990-05-01 | 30.15 | 31.7056 | 26.7476 | 24.5 | 25 | 25.5 | 27.2476 | 27.7476 | 3.4024 |  | 5.65 |  | 5.15 |  | 4.65 |  | 2.9024 |  | 2.4024
1990-05-02 | 31.3042 | 31.6493 | 26.7318 | 24.5 | 25 | 25.5 | 27.2318 | 27.7318 | 4.5724 |  | 6.8042 |  | 6.3042 |  | 5.8042 |  | 4.0724 |  | 3.5724
1990-05-03 | 32.775 | 31.6456 | 26.7308 | 24.5 | 25 | 25.5 | 27.2308 | 27.7308 | 6.0442 |  | 8.275 |  | 7.775 |  | 7.275 |  | 5.5442 |  | 5.0442
1990-05-04 | 33.4042 | 31.7186 | 26.7512 | 24.5 | 25 | 25.5 | 27.2512 | 27.7512 | 6.653 |  | 8.9042 |  | 8.4042 |  | 7.9042 |  | 6.153 |  | 5.653
1990-05-05 | 33.9417 | 31.7882 | 26.7707 | 24.5 | 25 | 25.5 | 27.2707 | 27.7707 | 7.171 |  | 9.4417 |  | 8.9417 |  | 8.4417 |  | 6.671 |  | 6.171
1990-05-06 | 31.2458 | 31.8993 | 26.8018 | 24.5 | 25 | 25.5 | 27.3018 | 27.8018 | 4.444 |  | 6.7458 |  | 6.2458 |  | 5.7458 |  | 3.944 |  | 3.444
1990-05-07 | 32.6292 | 31.8894 | 26.799 | 24.5 | 25 | 25.5 | 27.299 | 27.799 | 5.8301 |  | 8.1292 |  | 7.6292 |  | 7.1292 |  | 5.3301 |  | 4.8301
1990-05-08 | 32.2917 | 31.9411 | 26.8135 | 24.5 | 25 | 25.5 | 27.3135 | 27.8135 | 5.4782 |  | 7.7917 |  | 7.2917 |  | 6.7917 |  | 4.9782 |  | 4.4782
1990-05-09 | 33.4208 | 31.9521 | 26.8166 | 24.5 | 25 | 25.5 | 27.3166 | 27.8166 | 6.6042 |  | 8.9208 |  | 8.4208 |  | 7.9208 |  | 6.1042 |  | 5.6042
1990-05-10 | 33.7542 | 31.9629 | 26.8196 | 24.5 | 25 | 25.5 | 27.3196 | 27.8196 | 6.9346 |  | 9.2542 |  | 8.7542 |  | 8.2542 |  | 6.4346 |  | 5.9346
1990-05-11 | 32.2542 | 31.9844 | 26.8256 | 24.5 | 25 | 25.5 | 27.3256 | 27.8256 | 5.4285 |  | 7.7542 |  | 7.2542 |  | 6.7542 |  | 4.9285 |  | 4.4285
1990-05-12 | 32.9417 | 31.951 | 26.8163 | 24.5 | 25 | 25.5 | 27.3163 | 27.8163 | 6.1254 |  | 8.4417 |  | 7.9417 |  | 7.4417 |  | 5.6254 |  | 5.1254
1990-05-13 | 32.9583 | 31.9471 | 26.8152 | 24.5 | 25 | 25.5 | 27.3152 | 27.8152 | 6.1431 |  | 8.4583 |  | 7.9583 |  | 7.4583 |  | 5.6431 |  | 5.1431
1990-05-14 | 33 | 31.9182 | 26.8071 | 24.5 | 25 | 25.5 | 27.3071 | 27.8071 | 6.1929 |  | 8.5 |  | 8 |  | 7.5 |  | 5.6929 |  | 5.1929
1990-05-15 | 33.7958 | 31.8993 | 26.8018 | 24.5 | 25 | 25.5 | 27.3018 | 27.8018 | 6.994 |  | 9.2958 |  | 8.7958 |  | 8.2958 |  | 6.494 |  | 5.994
1990-05-16 | 33.1833 | 31.8908 | 26.7994 | 24.5 | 25 | 25.5 | 27.2994 | 27.7994 | 6.3839 |  | 8.6833 |  | 8.1833 |  | 7.6833 |  | 5.8839 |  | 5.3839
1990-05-17 | 33.7458 | 31.8583 | 26.7903 | 24.5 | 25 | 25.5 | 27.2903 | 27.7903 | 6.9555 |  | 9.2458 |  | 8.7458 |  | 8.2458 |  | 6.4555 |  | 5.9555
1990-05-18 | 34.0167 | 31.9168 | 26.8067 | 24.5 | 25 | 25.5 | 27.3067 | 27.8067 | 7.21 |  | 9.5167 |  | 9.0167 |  | 8.5167 |  | 6.71 |  | 6.21
1990-05-19 | 34.725 | 31.9272 | 26.8096 | 24.5 | 25 | 25.5 | 27.3096 | 27.8096 | 7.9154 |  | 10.225 |  | 9.725 |  | 9.225 |  | 7.4154 |  | 6.9154
1990-05-20 | 34.4 | 31.995 | 26.8286 | 24.5 | 25 | 25.5 | 27.3286 | 27.8286 | 7.5714 |  | 9.9 |  | 9.4 |  | 8.9 |  | 7.0714 |  | 6.5714
1990-05-21 | 33.8208 | 32.1729 | 26.8784 | 24.5 | 25 | 25.5 | 27.3784 | 27.8784 | 6.9424 |  | 9.3208 |  | 8.8208 |  | 8.3208 |  | 6.4424 |  | 5.9424
1990-05-22 | 34.5042 | 32.2844 | 26.9096 | 24.5 | 25 | 25.5 | 27.4096 | 27.9096 | 7.5945 |  | 10.0042 |  | 9.5042 |  | 9.0042 |  | 7.0945 |  | 6.5945
1990-05-23 | 35.0375 | 32.4263 | 26.9494 | 24.5 | 25 | 25.5 | 27.4494 | 27.9494 | 8.0881 |  | 10.5375 |  | 10.0375 |  | 9.5375 |  | 7.5881 |  | 7.0881
1990-05-24 | 33.675 | 32.5289 | 26.9781 | 24.5 | 25 | 25.5 | 27.4781 | 27.9781 | 6.6969 |  | 9.175 |  | 8.675 |  | 8.175 |  | 6.1969 |  | 5.6969
1990-05-25 | 32.9375 | 32.616 | 27.0025 | 24.5 | 25 | 25.5 | 27.5025 | 28.0025 | 5.935 |  | 8.4375 |  | 7.9375 |  | 7.4375 |  | 5.435 |  | 4.935
1990-05-26 | 33.4167 | 32.7306 | 27.0346 | 24.5 | 25 | 25.5 | 27.5346 | 28.0346 | 6.3821 |  | 8.9167 |  | 8.4167 |  | 7.9167 |  | 5.8821 |  | 5.3821
1990-05-27 | 31.6458 | 32.8943 | 27.0804 | 24.5 | 25 | 25.5 | 27.5804 | 28.0804 | 4.5654 |  | 7.1458 |  | 6.6458 |  | 6.1458 |  | 4.0654 |  | 3.5654
1990-05-28 | 31.8542 | 32.9463 | 27.095 | 24.5 | 25 | 25.5 | 27.595 | 28.095 | 4.7592 |  | 7.3542 |  | 6.8542 |  | 6.3542 |  | 4.2592 |  | 3.7592
1990-05-29 | 33.0458 | 33.0017 | 27.1105 | 24.5 | 25 | 25.5 | 27.6105 | 28.1105 | 5.9354 |  | 8.5458 |  | 8.0458 |  | 7.5458 |  | 5.4354 |  | 4.9354
1990-05-30 | 31.0083 | 33.0694 | 27.1294 | 24.5 | 25 | 25.5 | 27.6294 | 28.1294 | 3.8789 |  | 6.5083 |  | 6.0083 |  | 5.5083 |  | 3.3789 |  | 2.8789
1990-05-31 | 29.4458 | 33.0294 | 27.1182 | 24.5 | 25 | 25.5 | 27.6182 | 28.1182 | 2.3276 |  | 4.9458 |  | 4.4458 |  | 3.9458 |  | 1.8276 |  | 1.3276
1990-06-01 | 28.5042 | 33.006 | 27.1117 | 24.5 | 25 | 25.5 | 27.6117 | 28.1117 | 1.3925 |  | 4.0042 |  | 3.5042 |  | 3.0042 |  | 0.89249 |  | 0.39249
1990-06-02 | 29.025 | 32.9126 | 27.0855 | 24.5 | 25 | 25.5 | 27.5855 | 28.0855 | 1.9395 |  | 4.525 |  | 4.025 |  | 3.525 |  | 1.4395 |  | 0.93946
1990-06-03 | 30.2333 | 32.7876 | 27.0505 | 24.5 | 25 | 25.5 | 27.5505 | 28.0505 | 3.1828 |  | 5.7333 |  | 5.2333 |  | 4.7333 |  | 2.6828 |  | 2.1828
1990-06-04 | 30.5167 | 32.6819 | 27.0209 | 24.5 | 25 | 25.5 | 27.5209 | 28.0209 | 3.4957 |  | 6.0167 |  | 5.5167 |  | 5.0167 |  | 2.9957 |  | 2.4957
1990-06-05 | 31.7 | 32.5678 | 26.989 | 24.5 | 25 | 25.5 | 27.489 | 27.989 | 4.711 |  | 7.2 |  | 6.7 |  | 6.2 |  | 4.211 |  | 3.711
1990-06-06 | 32.6958 | 32.5829 | 26.9932 | 24.5 | 25 | 25.5 | 27.4932 | 27.9932 | 5.7026 |  | 8.1958 |  | 7.6958 |  | 7.1958 |  | 5.2026 |  | 4.7026
1990-06-07 | 33.2625 | 32.5851 | 26.9938 | 24.5 | 25 | 25.5 | 27.4938 | 27.9938 | 6.2687 |  | 8.7625 |  | 8.2625 |  | 7.7625 |  | 5.7687 |  | 5.2687
1990-06-08 | 33.2333 | 32.6175 | 27.0029 | 24.5 | 25 | 25.5 | 27.5029 | 28.0029 | 6.2304 |  | 8.7333 |  | 8.2333 |  | 7.7333 |  | 5.7304 |  | 5.2304
1990-06-09 | 33.1292 | 32.6113 | 27.0012 | 24.5 | 25 | 25.5 | 27.5012 | 28.0012 | 6.128 |  | 8.6292 |  | 8.1292 |  | 7.6292 |  | 5.628 |  | 5.128
1990-06-10 | 30.6833 | 32.5904 | 26.9953 | 24.5 | 25 | 25.5 | 27.4953 | 27.9953 | 3.688 |  | 6.1833 |  | 5.6833 |  | 5.1833 |  | 3.188 |  | 2.688
1990-06-11 | 31.375 | 32.5381 | 26.9807 | 24.5 | 25 | 25.5 | 27.4807 | 27.9807 | 4.3943 |  | 6.875 |  | 6.375 |  | 5.875 |  | 3.8943 |  | 3.3943
1990-06-12 | 30.6875 | 32.4858 | 26.966 | 24.5 | 25 | 25.5 | 27.466 | 27.966 | 3.7215 |  | 6.1875 |  | 5.6875 |  | 5.1875 |  | 3.2215 |  | 2.7215
1990-06-13 | 31.5667 | 32.4101 | 26.9448 | 24.5 | 25 | 25.5 | 27.4448 | 27.9448 | 4.6218 |  | 7.0667 |  | 6.5667 |  | 6.0667 |  | 4.1218 |  | 3.6218
1990-06-14 | 26.1417 | 32.3624 | 26.9315 | 24.5 | 25 | 25.5 | 27.4315 | 27.9315 | 0 |  | 1.6417 |  | 1.1417 |  | 0.64167 |  | 0 |  | 0
1990-06-15 | 29.2 | 32.1072 | 26.86 | 24.5 | 25 | 25.5 | 27.36 | 27.86 | 2.34 |  | 4.7 |  | 4.2 |  | 3.7 |  | 1.84 |  | 1.34
1990-06-16 | 25.8833 | 31.9744 | 26.8228 | 24.5 | 25 | 25.5 | 27.3228 | 27.8228 | 0 |  | 1.3833 |  | 0.88333 |  | 0.38333 |  | 0 |  | 0
1990-06-17 | 27.3 | 31.7124 | 26.7495 | 24.5 | 25 | 25.5 | 27.2495 | 27.7495 | 0.55054 |  | 2.8 |  | 2.3 |  | 1.8 |  | 0.050539 |  | 0
1990-06-18 | 28.35 | 31.4885 | 26.6868 | 24.5 | 25 | 25.5 | 27.1868 | 27.6868 | 1.6632 |  | 3.85 |  | 3.35 |  | 2.85 |  | 1.1632 |  | 0.66323
1990-06-19 | 26.5625 | 31.276 | 26.6273 | 24.5 | 25 | 25.5 | 27.1273 | 27.6273 | 0 |  | 2.0625 |  | 1.5625 |  | 1.0625 |  | 0 |  | 0
1990-06-20 | 24.1458 | 31.0147 | 26.5541 | 24.5 | 25 | 25.5 | 27.0541 | 27.5541 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-06-21 | 25.4917 | 30.6922 | 26.4638 | 24.5 | 25 | 25.5 | 26.9638 | 27.4638 | 0 |  | 0.99167 |  | 0.49167 |  | 0 |  | 0 |  | 0
1990-06-22 | 26.5042 | 30.3918 | 26.3797 | 24.5 | 25 | 25.5 | 26.8797 | 27.3797 | 0.12446 |  | 2.0042 |  | 1.5042 |  | 1.0042 |  | 0 |  | 0
1990-06-23 | 27.5 | 30.1074 | 26.3001 | 24.5 | 25 | 25.5 | 26.8001 | 27.3001 | 1.1999 |  | 3 |  | 2.5 |  | 2 |  | 0.69994 |  | 0.19994
1990-06-24 | 27.2083 | 29.9015 | 26.2424 | 24.5 | 25 | 25.5 | 26.7424 | 27.2424 | 0.96591 |  | 2.7083 |  | 2.2083 |  | 1.7083 |  | 0.46591 |  | 0
1990-06-25 | 27.3458 | 29.7106 | 26.189 | 24.5 | 25 | 25.5 | 26.689 | 27.189 | 1.1569 |  | 2.8458 |  | 2.3458 |  | 1.8458 |  | 0.65688 |  | 0.15688
1990-06-26 | 27.6417 | 29.5082 | 26.1323 | 24.5 | 25 | 25.5 | 26.6323 | 27.1323 | 1.5094 |  | 3.1417 |  | 2.6417 |  | 2.1417 |  | 1.0094 |  | 0.50937
1990-06-27 | 25.4792 | 29.3747 | 26.0949 | 24.5 | 25 | 25.5 | 26.5949 | 27.0949 | 0 |  | 0.97917 |  | 0.47917 |  | 0 |  | 0 |  | 0
1990-06-28 | 24.725 | 29.1622 | 26.0354 | 24.5 | 25 | 25.5 | 26.5354 | 27.0354 | 0 |  | 0.225 |  | 0 |  | 0 |  | 0 |  | 0
1990-06-29 | 24.975 | 28.8849 | 25.9578 | 24.5 | 25 | 25.5 | 26.4578 | 26.9578 | 0 |  | 0.475 |  | 0 |  | 0 |  | 0 |  | 0
1990-06-30 | 26.5083 | 28.6837 | 25.9015 | 24.5 | 25 | 25.5 | 26.4015 | 26.9015 | 0.60688 |  | 2.0083 |  | 1.5083 |  | 1.0083 |  | 0.10688 |  | 0
1990-07-01 | 28.2125 | 28.5858 | 25.874 | 24.5 | 25 | 25.5 | 26.374 | 26.874 | 2.3385 |  | 3.7125 |  | 3.2125 |  | 2.7125 |  | 1.8385 |  | 1.3385
1990-07-02 | 26.4125 | 28.5761 | 25.8713 | 24.5 | 25 | 25.5 | 26.3713 | 26.8713 | 0.54119 |  | 1.9125 |  | 1.4125 |  | 0.9125 |  | 0.041189 |  | 0
1990-07-03 | 26.8625 | 28.489 | 25.8469 | 24.5 | 25 | 25.5 | 26.3469 | 26.8469 | 1.0156 |  | 2.3625 |  | 1.8625 |  | 1.3625 |  | 0.51557 |  | 0.015572
1990-07-04 | 24.8 | 28.3767 | 25.8155 | 24.5 | 25 | 25.5 | 26.3155 | 26.8155 | 0 |  | 0.3 |  | 0 |  | 0 |  | 0 |  | 0
1990-07-05 | 23.4958 | 28.1861 | 25.7621 | 24.5 | 25 | 25.5 | 26.2621 | 26.7621 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-07-06 | 23.6583 | 27.9126 | 25.6855 | 24.5 | 25 | 25.5 | 26.1855 | 26.6855 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-07-07 | 24.0208 | 27.6114 | 25.6012 | 24.5 | 25 | 25.5 | 26.1012 | 26.6012 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-07-08 | 23.2708 | 27.3033 | 25.5149 | 24.5 | 25 | 25.5 | 26.0149 | 26.5149 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-07-09 | 24.0792 | 26.9712 | 25.4219 | 24.5 | 25 | 25.5 | 25.9219 | 26.4219 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-07-10 | 25.0417 | 26.6696 | 25.3375 | 24.5 | 25 | 25.5 | 25.8375 | 26.3375 | 0 |  | 0.54167 |  | 0.041667 |  | 0 |  | 0 |  | 0
1990-07-11 | 26.4458 | 26.4815 | 25.2848 | 24.5 | 25 | 25.5 | 25.7848 | 26.2848 | 1.161 |  | 1.9458 |  | 1.4458 |  | 0.94583 |  | 0.66101 |  | 0.16101
1990-07-12 | 27.5167 | 26.3172 | 25.2388 | 24.5 | 25 | 25.5 | 25.7388 | 26.2388 | 2.2778 |  | 3.0167 |  | 2.5167 |  | 2.0167 |  | 1.7778 |  | 1.2778
1990-07-13 | 26.825 | 26.2115 | 25.2092 | 24.5 | 25 | 25.5 | 25.7092 | 26.2092 | 1.6158 |  | 2.325 |  | 1.825 |  | 1.325 |  | 1.1158 |  | 0.61577
1990-07-14 | 28.3708 | 26.0535 | 25.165 | 24.5 | 25 | 25.5 | 25.665 | 26.165 | 3.2059 |  | 3.8708 |  | 3.3708 |  | 2.8708 |  | 2.7059 |  | 2.2059
1990-07-15 | 28.1458 | 26.1278 | 25.1858 | 24.5 | 25 | 25.5 | 25.6858 | 26.1858 | 2.9601 |  | 3.6458 |  | 3.1458 |  | 2.6458 |  | 2.4601 |  | 1.9601
1990-07-16 | 27.9042 | 26.0926 | 25.1759 | 24.5 | 25 | 25.5 | 25.6759 | 26.1759 | 2.7282 |  | 3.4042 |  | 2.9042 |  | 2.4042 |  | 2.2282 |  | 1.7282
1990-07-17 | 28.425 | 26.16 | 25.1948 | 24.5 | 25 | 25.5 | 25.6948 | 26.1948 | 3.2302 |  | 3.925 |  | 3.425 |  | 2.925 |  | 2.7302 |  | 2.2302
1990-07-18 | 28.7792 | 26.1975 | 25.2053 | 24.5 | 25 | 25.5 | 25.7053 | 26.2053 | 3.5739 |  | 4.2792 |  | 3.7792 |  | 3.2792 |  | 3.0739 |  | 2.5739
1990-07-19 | 27.2333 | 26.2118 | 25.2093 | 24.5 | 25 | 25.5 | 25.7093 | 26.2093 | 2.024 |  | 2.7333 |  | 2.2333 |  | 1.7333 |  | 1.524 |  | 1.024
1990-07-20 | 27.6417 | 26.2342 | 25.2156 | 24.5 | 25 | 25.5 | 25.7156 | 26.2156 | 2.4261 |  | 3.1417 |  | 2.6417 |  | 2.1417 |  | 1.9261 |  | 1.4261
1990-07-21 | 27.1 | 26.3507 | 25.2482 | 24.5 | 25 | 25.5 | 25.7482 | 26.2482 | 1.8518 |  | 2.6 |  | 2.1 |  | 1.6 |  | 1.3518 |  | 0.85181
1990-07-22 | 26.5625 | 26.4043 | 25.2632 | 24.5 | 25 | 25.5 | 25.7632 | 26.2632 | 1.2993 |  | 2.0625 |  | 1.5625 |  | 1.0625 |  | 0.79929 |  | 0.29929
1990-07-23 | 27.125 | 26.4062 | 25.2638 | 24.5 | 25 | 25.5 | 25.7638 | 26.2638 | 1.8612 |  | 2.625 |  | 2.125 |  | 1.625 |  | 1.3612 |  | 0.86125
1990-07-24 | 27.1167 | 26.3937 | 25.2602 | 24.5 | 25 | 25.5 | 25.7602 | 26.2602 | 1.8564 |  | 2.6167 |  | 2.1167 |  | 1.6167 |  | 1.3564 |  | 0.85642
1990-07-25 | 27.3333 | 26.3907 | 25.2594 | 24.5 | 25 | 25.5 | 25.7594 | 26.2594 | 2.0739 |  | 2.8333 |  | 2.3333 |  | 1.8333 |  | 1.5739 |  | 1.0739
1990-07-26 | 26.95 | 26.3903 | 25.2593 | 24.5 | 25 | 25.5 | 25.7593 | 26.2593 | 1.6907 |  | 2.45 |  | 1.95 |  | 1.45 |  | 1.1907 |  | 0.69072
1990-07-27 | 28.5208 | 26.3672 | 25.2528 | 24.5 | 25 | 25.5 | 25.7528 | 26.2528 | 3.268 |  | 4.0208 |  | 3.5208 |  | 3.0208 |  | 2.768 |  | 2.268
1990-07-28 | 27.0917 | 26.4686 | 25.2812 | 24.5 | 25 | 25.5 | 25.7812 | 26.2812 | 1.8105 |  | 2.5917 |  | 2.0917 |  | 1.5917 |  | 1.3105 |  | 0.81046
1990-07-29 | 27.0417 | 26.5475 | 25.3033 | 24.5 | 25 | 25.5 | 25.8033 | 26.3033 | 1.7384 |  | 2.5417 |  | 2.0417 |  | 1.5417 |  | 1.2384 |  | 0.73837
1990-07-30 | 29.0375 | 26.6164 | 25.3226 | 24.5 | 25 | 25.5 | 25.8226 | 26.3226 | 3.7149 |  | 4.5375 |  | 4.0375 |  | 3.5375 |  | 3.2149 |  | 2.7149
1990-07-31 | 29.1625 | 26.7007 | 25.3462 | 24.5 | 25 | 25.5 | 25.8462 | 26.3462 | 3.8163 |  | 4.6625 |  | 4.1625 |  | 3.6625 |  | 3.3163 |  | 2.8163
1990-08-01 | 27.8542 | 26.7324 | 25.3551 | 24.5 | 25 | 25.5 | 25.8551 | 26.3551 | 2.4991 |  | 3.3542 |  | 2.8542 |  | 2.3542 |  | 1.9991 |  | 1.4991
1990-08-02 | 26.8417 | 26.7804 | 25.3685 | 24.5 | 25 | 25.5 | 25.8685 | 26.3685 | 1.4732 |  | 2.3417 |  | 1.8417 |  | 1.3417 |  | 0.97315 |  | 0.47315
1990-08-03 | 26.1875 | 26.7797 | 25.3683 | 24.5 | 25 | 25.5 | 25.8683 | 26.3683 | 0.81918 |  | 1.6875 |  | 1.1875 |  | 0.6875 |  | 0.31918 |  | 0
1990-08-04 | 25.8083 | 26.826 | 25.3813 | 24.5 | 25 | 25.5 | 25.8813 | 26.3813 | 0.42706 |  | 1.3083 |  | 0.80833 |  | 0.30833 |  | 0 |  | 0
1990-08-05 | 24.7167 | 26.9031 | 25.4029 | 24.5 | 25 | 25.5 | 25.9029 | 26.4029 | 0 |  | 0.21667 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-06 | 23.8125 | 26.9383 | 25.4127 | 24.5 | 25 | 25.5 | 25.9127 | 26.4127 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-07 | 24.5208 | 26.9314 | 25.4108 | 24.5 | 25 | 25.5 | 25.9108 | 26.4108 | 0 |  | 0.020833 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-08 | 25.1042 | 26.9731 | 25.4225 | 24.5 | 25 | 25.5 | 25.9225 | 26.4225 | 0 |  | 0.60417 |  | 0.10417 |  | 0 |  | 0 |  | 0
1990-08-09 | 25.3708 | 27.0072 | 25.432 | 24.5 | 25 | 25.5 | 25.932 | 26.432 | 0 |  | 0.87083 |  | 0.37083 |  | 0 |  | 0 |  | 0
1990-08-10 | 26.2542 | 27.0182 | 25.4351 | 24.5 | 25 | 25.5 | 25.9351 | 26.4351 | 0.81907 |  | 1.7542 |  | 1.2542 |  | 0.75417 |  | 0.31907 |  | 0
1990-08-11 | 26.0667 | 27.0118 | 25.4333 | 24.5 | 25 | 25.5 | 25.9333 | 26.4333 | 0.63336 |  | 1.5667 |  | 1.0667 |  | 0.56667 |  | 0.13336 |  | 0
1990-08-12 | 24.4375 | 26.9635 | 25.4198 | 24.5 | 25 | 25.5 | 25.9198 | 26.4198 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-13 | 25.3292 | 26.8839 | 25.3975 | 24.5 | 25 | 25.5 | 25.8975 | 26.3975 | 0 |  | 0.82917 |  | 0.32917 |  | 0 |  | 0 |  | 0
1990-08-14 | 26.5042 | 26.7825 | 25.3691 | 24.5 | 25 | 25.5 | 25.8691 | 26.3691 | 1.1351 |  | 2.0042 |  | 1.5042 |  | 1.0042 |  | 0.63507 |  | 0.13507
1990-08-15 | 25.7583 | 26.7278 | 25.3538 | 24.5 | 25 | 25.5 | 25.8538 | 26.3538 | 0.40456 |  | 1.2583 |  | 0.75833 |  | 0.25833 |  | 0 |  | 0
1990-08-16 | 25.0333 | 26.6563 | 25.3338 | 24.5 | 25 | 25.5 | 25.8338 | 26.3338 | 0 |  | 0.53333 |  | 0.033333 |  | 0 |  | 0 |  | 0
1990-08-17 | 24.7125 | 26.5432 | 25.3021 | 24.5 | 25 | 25.5 | 25.8021 | 26.3021 | 0 |  | 0.2125 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-18 | 25.1458 | 26.4076 | 25.2641 | 24.5 | 25 | 25.5 | 25.7641 | 26.2641 | 0 |  | 0.64583 |  | 0.14583 |  | 0 |  | 0 |  | 0
1990-08-19 | 25.85 | 26.3381 | 25.2447 | 24.5 | 25 | 25.5 | 25.7447 | 26.2447 | 0.60534 |  | 1.35 |  | 0.85 |  | 0.35 |  | 0.10534 |  | 0
1990-08-20 | 25.2875 | 26.2783 | 25.2279 | 24.5 | 25 | 25.5 | 25.7279 | 26.2279 | 0.059567 |  | 0.7875 |  | 0.2875 |  | 0 |  | 0 |  | 0
1990-08-21 | 24.75 | 26.2179 | 25.211 | 24.5 | 25 | 25.5 | 25.711 | 26.211 | 0 |  | 0.25 |  | 0 |  | 0 |  | 0 |  | 0
1990-08-22 | 25.7083 | 26.1575 | 25.1941 | 24.5 | 25 | 25.5 | 25.6941 | 26.1941 | 0.51423 |  | 1.2083 |  | 0.70833 |  | 0.20833 |  | 0.014233 |  | 0
1990-08-23 | 25.9625 | 26.1103 | 25.1809 | 24.5 | 25 | 25.5 | 25.6809 | 26.1809 | 0.78162 |  | 1.4625 |  | 0.9625 |  | 0.4625 |  | 0.28162 |  | 0
1990-08-24 | 26.1375 | 26.0718 | 25.1701 | 24.5 | 25 | 25.5 | 25.6701 | 26.1701 | 0.96739 |  | 1.6375 |  | 1.1375 |  | 0.6375 |  | 0.46739 |  | 0
1990-08-25 | 25.95 | 26.0319 | 25.1589 | 24.5 | 25 | 25.5 | 25.6589 | 26.1589 | 0.79106 |  | 1.45 |  | 0.95 |  | 0.45 |  | 0.29106 |  | 0
1990-08-26 | 25.525 | 25.9986 | 25.1496 | 24.5 | 25 | 25.5 | 25.6496 | 26.1496 | 0.37539 |  | 1.025 |  | 0.525 |  | 0.025 |  | 0 |  | 0
1990-08-27 | 25.6917 | 25.8988 | 25.1217 | 24.5 | 25 | 25.5 | 25.6217 | 26.1217 | 0.57002 |  | 1.1917 |  | 0.69167 |  | 0.19167 |  | 0.070017 |  | 0
1990-08-28 | 26.0208 | 25.8521 | 25.1086 | 24.5 | 25 | 25.5 | 25.6086 | 26.1086 | 0.91225 |  | 1.5208 |  | 1.0208 |  | 0.52083 |  | 0.41225 |  | 0
1990-08-29 | 26.6458 | 25.8181 | 25.0991 | 24.5 | 25 | 25.5 | 25.5991 | 26.0991 | 1.5468 |  | 2.1458 |  | 1.6458 |  | 1.1458 |  | 1.0468 |  | 0.54678
1990-08-30 | 26.3083 | 25.7383 | 25.0767 | 24.5 | 25 | 25.5 | 25.5767 | 26.0767 | 1.2316 |  | 1.8083 |  | 1.3083 |  | 0.80833 |  | 0.7316 |  | 0.2316
1990-08-31 | 27.1708 | 25.6432 | 25.0501 | 24.5 | 25 | 25.5 | 25.5501 | 26.0501 | 2.1207 |  | 2.6708 |  | 2.1708 |  | 1.6708 |  | 1.6207 |  | 1.1207
1990-09-01 | 26.425 | 25.6204 | 25.0437 | 24.5 | 25 | 25.5 | 25.5437 | 26.0437 | 1.3813 |  | 1.925 |  | 1.425 |  | 0.925 |  | 0.88128 |  | 0.38128
1990-09-02 | 26.2667 | 25.6065 | 25.0398 | 24.5 | 25 | 25.5 | 25.5398 | 26.0398 | 1.2268 |  | 1.7667 |  | 1.2667 |  | 0.76667 |  | 0.72684 |  | 0.22684
1990-09-03 | 26.0167 | 25.6092 | 25.0406 | 24.5 | 25 | 25.5 | 25.5406 | 26.0406 | 0.9761 |  | 1.5167 |  | 1.0167 |  | 0.51667 |  | 0.4761 |  | 0
1990-09-04 | 25.7417 | 25.6161 | 25.0425 | 24.5 | 25 | 25.5 | 25.5425 | 26.0425 | 0.69916 |  | 1.2417 |  | 0.74167 |  | 0.24167 |  | 0.19916 |  | 0
1990-09-05 | 24.8917 | 25.6503 | 25.0521 | 24.5 | 25 | 25.5 | 25.5521 | 26.0521 | 0 |  | 0.39167 |  | 0 |  | 0 |  | 0 |  | 0
1990-09-06 | 24.9167 | 25.6862 | 25.0621 | 24.5 | 25 | 25.5 | 25.5621 | 26.0621 | 0 |  | 0.41667 |  | 0 |  | 0 |  | 0 |  | 0
1990-09-07 | 25.6458 | 25.6994 | 25.0658 | 24.5 | 25 | 25.5 | 25.5658 | 26.0658 | 0.57999 |  | 1.1458 |  | 0.64583 |  | 0.14583 |  | 0.079989 |  | 0
1990-09-08 | 25.6708 | 25.7175 | 25.0709 | 24.5 | 25 | 25.5 | 25.5709 | 26.0709 | 0.59993 |  | 1.1708 |  | 0.67083 |  | 0.17083 |  | 0.099933 |  | 0
1990-09-09 | 26.2667 | 25.7275 | 25.0737 | 24.5 | 25 | 25.5 | 25.5737 | 26.0737 | 1.193 |  | 1.7667 |  | 1.2667 |  | 0.76667 |  | 0.69297 |  | 0.19297
1990-09-10 | 26.7042 | 25.7279 | 25.0738 | 24.5 | 25 | 25.5 | 25.5738 | 26.0738 | 1.6304 |  | 2.2042 |  | 1.7042 |  | 1.2042 |  | 1.1304 |  | 0.63035
1990-09-11 | 25.4917 | 25.7492 | 25.0798 | 24.5 | 25 | 25.5 | 25.5798 | 26.0798 | 0.4119 |  | 0.99167 |  | 0.49167 |  | 0 |  | 0 |  | 0
1990-09-12 | 26.225 | 25.7843 | 25.0896 | 24.5 | 25 | 25.5 | 25.5896 | 26.0896 | 1.1354 |  | 1.725 |  | 1.225 |  | 0.725 |  | 0.63539 |  | 0.13539
1990-09-13 | 26.2125 | 25.8142 | 25.098 | 24.5 | 25 | 25.5 | 25.598 | 26.098 | 1.1145 |  | 1.7125 |  | 1.2125 |  | 0.7125 |  | 0.61453 |  | 0.11453
1990-09-14 | 26.8167 | 25.8044 | 25.0952 | 24.5 | 25 | 25.5 | 25.5952 | 26.0952 | 1.7214 |  | 2.3167 |  | 1.8167 |  | 1.3167 |  | 1.2214 |  | 0.72142
1990-09-15 | 27.1083 | 25.8397 | 25.1051 | 24.5 | 25 | 25.5 | 25.6051 | 26.1051 | 2.0032 |  | 2.6083 |  | 2.1083 |  | 1.6083 |  | 1.5032 |  | 1.0032
1990-09-16 | 27.3708 | 25.9089 | 25.1245 | 24.5 | 25 | 25.5 | 25.6245 | 26.1245 | 2.2463 |  | 2.8708 |  | 2.3708 |  | 1.8708 |  | 1.7463 |  | 1.2463
1990-09-17 | 27.6333 | 25.9975 | 25.1493 | 24.5 | 25 | 25.5 | 25.6493 | 26.1493 | 2.484 |  | 3.1333 |  | 2.6333 |  | 2.1333 |  | 1.984 |  | 1.484
1990-09-18 | 27.8125 | 26.0804 | 25.1725 | 24.5 | 25 | 25.5 | 25.6725 | 26.1725 | 2.64 |  | 3.3125 |  | 2.8125 |  | 2.3125 |  | 2.14 |  | 1.64
1990-09-19 | 25.0333 | 26.1458 | 25.1908 | 24.5 | 25 | 25.5 | 25.6908 | 26.1908 | 0 |  | 0.53333 |  | 0.033333 |  | 0 |  | 0 |  | 0
1990-09-20 | 27.3375 | 26.1374 | 25.1885 | 24.5 | 25 | 25.5 | 25.6885 | 26.1885 | 2.149 |  | 2.8375 |  | 2.3375 |  | 1.8375 |  | 1.649 |  | 1.149
1990-09-21 | 26.5958 | 26.2236 | 25.2126 | 24.5 | 25 | 25.5 | 25.7126 | 26.2126 | 1.3832 |  | 2.0958 |  | 1.5958 |  | 1.0958 |  | 0.88322 |  | 0.38322
1990-09-22 | 27.4167 | 26.2532 | 25.2209 | 24.5 | 25 | 25.5 | 25.7209 | 26.2209 | 2.1958 |  | 2.9167 |  | 2.4167 |  | 1.9167 |  | 1.6958 |  | 1.1958
1990-09-23 | 25.6333 | 26.3017 | 25.2345 | 24.5 | 25 | 25.5 | 25.7345 | 26.2345 | 0.39887 |  | 1.1333 |  | 0.63333 |  | 0.13333 |  | 0 |  | 0
1990-09-24 | 25.8833 | 26.2849 | 25.2298 | 24.5 | 25 | 25.5 | 25.7298 | 26.2298 | 0.65357 |  | 1.3833 |  | 0.88333 |  | 0.38333 |  | 0.15357 |  | 0
1990-09-25 | 25.8458 | 26.2826 | 25.2291 | 24.5 | 25 | 25.5 | 25.7291 | 26.2291 | 0.61669 |  | 1.3458 |  | 0.84583 |  | 0.34583 |  | 0.11669 |  | 0
1990-09-26 | 26.8792 | 26.2933 | 25.2321 | 24.5 | 25 | 25.5 | 25.7321 | 26.2321 | 1.647 |  | 2.3792 |  | 1.8792 |  | 1.3792 |  | 1.147 |  | 0.64703
1990-09-27 | 27.1 | 26.3329 | 25.2432 | 24.5 | 25 | 25.5 | 25.7432 | 26.2432 | 1.8568 |  | 2.6 |  | 2.1 |  | 1.6 |  | 1.3568 |  | 0.85678
1990-09-28 | 25.4083 | 26.3689 | 25.2533 | 24.5 | 25 | 25.5 | 25.7533 | 26.2533 | 0.15504 |  | 0.90833 |  | 0.40833 |  | 0 |  | 0 |  | 0
1990-09-29 | 25.3625 | 26.3276 | 25.2417 | 24.5 | 25 | 25.5 | 25.7417 | 26.2417 | 0.12076 |  | 0.8625 |  | 0.3625 |  | 0 |  | 0 |  | 0
1990-09-30 | 24.0792 | 26.2961 | 25.2329 | 24.5 | 25 | 25.5 | 25.7329 | 26.2329 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-01 | 27.2417 | 26.1931 | 25.2041 | 24.5 | 25 | 25.5 | 25.7041 | 26.2041 | 2.0376 |  | 2.7417 |  | 2.2417 |  | 1.7417 |  | 1.5376 |  | 1.0376
1990-10-02 | 27.9833 | 26.2203 | 25.2117 | 24.5 | 25 | 25.5 | 25.7117 | 26.2117 | 2.7717 |  | 3.4833 |  | 2.9833 |  | 2.4833 |  | 2.2717 |  | 1.7717
1990-10-03 | 26.3292 | 26.2775 | 25.2277 | 24.5 | 25 | 25.5 | 25.7277 | 26.2277 | 1.1015 |  | 1.8292 |  | 1.3292 |  | 0.82917 |  | 0.60147 |  | 0.10147
1990-10-04 | 27.0708 | 26.2879 | 25.2306 | 24.5 | 25 | 25.5 | 25.7306 | 26.2306 | 1.8402 |  | 2.5708 |  | 2.0708 |  | 1.5708 |  | 1.3402 |  | 0.84022
1990-10-05 | 28.0542 | 26.3322 | 25.243 | 24.5 | 25 | 25.5 | 25.743 | 26.243 | 2.8111 |  | 3.5542 |  | 3.0542 |  | 2.5542 |  | 2.3111 |  | 1.8111
1990-10-06 | 27.8083 | 26.4376 | 25.2725 | 24.5 | 25 | 25.5 | 25.7725 | 26.2725 | 2.5358 |  | 3.3083 |  | 2.8083 |  | 2.3083 |  | 2.0358 |  | 1.5358
1990-10-07 | 25.9667 | 26.534 | 25.2995 | 24.5 | 25 | 25.5 | 25.7995 | 26.2995 | 0.66714 |  | 1.4667 |  | 0.96667 |  | 0.46667 |  | 0.16714 |  | 0
1990-10-08 | 26.8792 | 26.5447 | 25.3025 | 24.5 | 25 | 25.5 | 25.8025 | 26.3025 | 1.5766 |  | 2.3792 |  | 1.8792 |  | 1.3792 |  | 1.0766 |  | 0.57664
1990-10-09 | 27.2958 | 26.585 | 25.3138 | 24.5 | 25 | 25.5 | 25.8138 | 26.3138 | 1.982 |  | 2.7958 |  | 2.2958 |  | 1.7958 |  | 1.482 |  | 0.98203
1990-10-10 | 27.075 | 26.6193 | 25.3234 | 24.5 | 25 | 25.5 | 25.8234 | 26.3234 | 1.7516 |  | 2.575 |  | 2.075 |  | 1.575 |  | 1.2516 |  | 0.75159
1990-10-11 | 26.725 | 26.6317 | 25.3269 | 24.5 | 25 | 25.5 | 25.8269 | 26.3269 | 1.3981 |  | 2.225 |  | 1.725 |  | 1.225 |  | 0.89813 |  | 0.39813
1990-10-12 | 27.3208 | 26.6728 | 25.3384 | 24.5 | 25 | 25.5 | 25.8384 | 26.3384 | 1.9825 |  | 2.8208 |  | 2.3208 |  | 1.8208 |  | 1.4825 |  | 0.98246
1990-10-13 | 27.1667 | 26.7093 | 25.3486 | 24.5 | 25 | 25.5 | 25.8486 | 26.3486 | 1.8181 |  | 2.6667 |  | 2.1667 |  | 1.6667 |  | 1.3181 |  | 0.81806
1990-10-14 | 26.5667 | 26.7411 | 25.3575 | 24.5 | 25 | 25.5 | 25.8575 | 26.3575 | 1.2092 |  | 2.0667 |  | 1.5667 |  | 1.0667 |  | 0.70916 |  | 0.20916
1990-10-15 | 26.9375 | 26.7328 | 25.3552 | 24.5 | 25 | 25.5 | 25.8552 | 26.3552 | 1.5823 |  | 2.4375 |  | 1.9375 |  | 1.4375 |  | 1.0823 |  | 0.58232
1990-10-16 | 26.9583 | 26.7271 | 25.3536 | 24.5 | 25 | 25.5 | 25.8536 | 26.3536 | 1.6047 |  | 2.4583 |  | 1.9583 |  | 1.4583 |  | 1.1047 |  | 0.60475
1990-10-17 | 25.7792 | 26.7133 | 25.3497 | 24.5 | 25 | 25.5 | 25.8497 | 26.3497 | 0.42943 |  | 1.2792 |  | 0.77917 |  | 0.27917 |  | 0 |  | 0
1990-10-18 | 26.2917 | 26.6515 | 25.3324 | 24.5 | 25 | 25.5 | 25.8324 | 26.3324 | 0.95924 |  | 1.7917 |  | 1.2917 |  | 0.79167 |  | 0.45924 |  | 0
1990-10-19 | 26.4333 | 26.6008 | 25.3182 | 24.5 | 25 | 25.5 | 25.8182 | 26.3182 | 1.1151 |  | 1.9333 |  | 1.4333 |  | 0.93333 |  | 0.6151 |  | 0.1151
1990-10-20 | 26.5708 | 26.6475 | 25.3313 | 24.5 | 25 | 25.5 | 25.8313 | 26.3313 | 1.2395 |  | 2.0708 |  | 1.5708 |  | 1.0708 |  | 0.73953 |  | 0.23953
1990-10-21 | 25.1833 | 26.6219 | 25.3241 | 24.5 | 25 | 25.5 | 25.8241 | 26.3241 | 0 |  | 0.68333 |  | 0.18333 |  | 0 |  | 0 |  | 0
1990-10-22 | 25.775 | 26.5749 | 25.311 | 24.5 | 25 | 25.5 | 25.811 | 26.311 | 0.46404 |  | 1.275 |  | 0.775 |  | 0.275 |  | 0 |  | 0
1990-10-23 | 24.8875 | 26.5201 | 25.2956 | 24.5 | 25 | 25.5 | 25.7956 | 26.2956 | 0 |  | 0.3875 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-24 | 24.475 | 26.4953 | 25.2887 | 24.5 | 25 | 25.5 | 25.7887 | 26.2887 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-25 | 23.3875 | 26.4483 | 25.2755 | 24.5 | 25 | 25.5 | 25.7755 | 26.2755 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-26 | 23.8958 | 26.3664 | 25.2526 | 24.5 | 25 | 25.5 | 25.7526 | 26.2526 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-27 | 24.0667 | 26.2669 | 25.2247 | 24.5 | 25 | 25.5 | 25.7247 | 26.2247 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-28 | 24.9542 | 26.1658 | 25.1964 | 24.5 | 25 | 25.5 | 25.6964 | 26.1964 | 0 |  | 0.45417 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-29 | 24.6917 | 26.1507 | 25.1922 | 24.5 | 25 | 25.5 | 25.6922 | 26.1922 | 0 |  | 0.19167 |  | 0 |  | 0 |  | 0 |  | 0
1990-10-30 | 25.25 | 26.1283 | 25.1859 | 24.5 | 25 | 25.5 | 25.6859 | 26.1859 | 0.064067 |  | 0.75 |  | 0.25 |  | 0 |  | 0 |  | 0
1990-10-31 | 24.3542 | 26.1674 | 25.1969 | 24.5 | 25 | 25.5 | 25.6969 | 26.1969 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-01 | 25.1208 | 26.0711 | 25.1699 | 24.5 | 25 | 25.5 | 25.6699 | 26.1699 | 0 |  | 0.62083 |  | 0.12083 |  | 0 |  | 0 |  | 0
1990-11-02 | 24.45 | 25.9757 | 25.1432 | 24.5 | 25 | 25.5 | 25.6432 | 26.1432 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-03 | 24.4875 | 25.9131 | 25.1257 | 24.5 | 25 | 25.5 | 25.6257 | 26.1257 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-04 | 24.1542 | 25.8269 | 25.1015 | 24.5 | 25 | 25.5 | 25.6015 | 26.1015 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-05 | 24.0458 | 25.6969 | 25.0651 | 24.5 | 25 | 25.5 | 25.5651 | 26.0651 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-06 | 23.4083 | 25.5715 | 25.03 | 24.5 | 25 | 25.5 | 25.53 | 26.03 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-07 | 23.0917 | 25.4862 | 25.0062 | 24.5 | 25 | 25.5 | 25.5062 | 26.0062 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-08 | 23.8458 | 25.36 | 24.9708 | 24.5 | 25 | 25.5 | 25.4708 | 25.9708 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-09 | 22.3458 | 25.245 | 24.9386 | 24.5 | 25 | 25.5 | 25.4386 | 25.9386 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-10 | 25.1125 | 25.0874 | 24.8945 | 24.5 | 25 | 25.5 | 25.3945 | 25.8945 | 0.21804 |  | 0.6125 |  | 0.1125 |  | 0 |  | 0 |  | 0
1990-11-11 | 24.9792 | 25.0336 | 24.8794 | 24.5 | 25 | 25.5 | 25.3794 | 25.8794 | 0.099756 |  | 0.47917 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-12 | 24.2042 | 24.9556 | 24.8576 | 24.5 | 25 | 25.5 | 25.3576 | 25.8576 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-13 | 23.0667 | 24.8568 | 24.8299 | 24.5 | 25 | 25.5 | 25.3299 | 25.8299 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-14 | 23.9208 | 24.7401 | 24.7972 | 24.5 | 25 | 25.5 | 25.2972 | 25.7972 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-15 | 25.3042 | 24.6396 | 24.7691 | 24.5 | 25 | 25.5 | 25.2691 | 25.7691 | 0.53508 |  | 0.80417 |  | 0.30417 |  | 0 |  | 0.035083 |  | 0
1990-11-16 | 24.1875 | 24.5844 | 24.7536 | 24.5 | 25 | 25.5 | 25.2536 | 25.7536 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-17 | 24.6042 | 24.5314 | 24.7388 | 24.5 | 25 | 25.5 | 25.2388 | 25.7388 | 0 |  | 0.10417 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-18 | 23.7375 | 24.4751 | 24.723 | 24.5 | 25 | 25.5 | 25.223 | 25.723 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-19 | 23.4708 | 24.3853 | 24.6979 | 24.5 | 25 | 25.5 | 25.1979 | 25.6979 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-20 | 24.0083 | 24.2819 | 24.6689 | 24.5 | 25 | 25.5 | 25.1689 | 25.6689 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-21 | 23.1625 | 24.2428 | 24.658 | 24.5 | 25 | 25.5 | 25.158 | 25.658 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-22 | 22.85 | 24.1557 | 24.6336 | 24.5 | 25 | 25.5 | 25.1336 | 25.6336 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-23 | 23.3292 | 24.0878 | 24.6146 | 24.5 | 25 | 25.5 | 25.1146 | 25.6146 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-24 | 23.0083 | 24.0496 | 24.6039 | 24.5 | 25 | 25.5 | 25.1039 | 25.6039 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-25 | 23.2333 | 24.0369 | 24.6003 | 24.5 | 25 | 25.5 | 25.1003 | 25.6003 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-26 | 23.2958 | 24.0149 | 24.5942 | 24.5 | 25 | 25.5 | 25.0942 | 25.5942 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-27 | 23.6958 | 23.9892 | 24.587 | 24.5 | 25 | 25.5 | 25.087 | 25.587 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-28 | 23.1 | 23.9472 | 24.5752 | 24.5 | 25 | 25.5 | 25.0752 | 25.5752 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-29 | 22.125 | 23.8942 | 24.5604 | 24.5 | 25 | 25.5 | 25.0604 | 25.5604 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-11-30 | 22.0542 | 23.79 | 24.5312 | 24.5 | 25 | 25.5 | 25.0312 | 25.5312 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-01 | 20.95 | 23.7133 | 24.5097 | 24.5 | 25 | 25.5 | 25.0097 | 25.5097 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-02 | 21.3417 | 23.5743 | 24.4708 | 24.5 | 25 | 25.5 | 24.9708 | 25.4708 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-03 | 21.7042 | 23.4707 | 24.4418 | 24.5 | 25 | 25.5 | 24.9418 | 25.4418 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-04 | 23.7625 | 23.3779 | 24.4158 | 24.5 | 25 | 25.5 | 24.9158 | 25.4158 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-05 | 24.4125 | 23.3649 | 24.4122 | 24.5 | 25 | 25.5 | 24.9122 | 25.4122 | 0.00033889 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-06 | 23.8458 | 23.3771 | 24.4156 | 24.5 | 25 | 25.5 | 24.9156 | 25.4156 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-07 | 23.0375 | 23.3917 | 24.4197 | 24.5 | 25 | 25.5 | 24.9197 | 25.4197 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-08 | 21.775 | 23.3899 | 24.4192 | 24.5 | 25 | 25.5 | 24.9192 | 25.4192 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-09 | 21.5917 | 23.3208 | 24.3998 | 24.5 | 25 | 25.5 | 24.8998 | 25.3998 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-10 | 21.825 | 23.2957 | 24.3928 | 24.5 | 25 | 25.5 | 24.8928 | 25.3928 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-11 | 23.225 | 23.1861 | 24.3621 | 24.5 | 25 | 25.5 | 24.8621 | 25.3621 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-12 | 23.3458 | 23.1276 | 24.3457 | 24.5 | 25 | 25.5 | 24.8457 | 25.3457 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-13 | 24.2583 | 23.099 | 24.3377 | 24.5 | 25 | 25.5 | 24.8377 | 25.3377 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-14 | 23.0833 | 23.1388 | 24.3489 | 24.5 | 25 | 25.5 | 24.8489 | 25.3489 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-15 | 21.8125 | 23.1108 | 24.341 | 24.5 | 25 | 25.5 | 24.841 | 25.341 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-16 | 20.1167 | 22.9944 | 24.3084 | 24.5 | 25 | 25.5 | 24.8084 | 25.3084 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-17 | 19.5667 | 22.8587 | 24.2705 | 24.5 | 25 | 25.5 | 24.7705 | 25.2705 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-18 | 19.175 | 22.6908 | 24.2234 | 24.5 | 25 | 25.5 | 24.7234 | 25.2234 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-19 | 18.375 | 22.5387 | 24.1808 | 24.5 | 25 | 25.5 | 24.6808 | 25.1808 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-20 | 18.5333 | 22.3689 | 24.1333 | 24.5 | 25 | 25.5 | 24.6333 | 25.1333 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-21 | 20.2458 | 22.1864 | 24.0822 | 24.5 | 25 | 25.5 | 24.5822 | 25.0822 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-22 | 21.5417 | 22.0892 | 24.055 | 24.5 | 25 | 25.5 | 24.555 | 25.055 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-23 | 22.9917 | 22.0456 | 24.0428 | 24.5 | 25 | 25.5 | 24.5428 | 25.0428 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-24 | 23.3583 | 22.0343 | 24.0396 | 24.5 | 25 | 25.5 | 24.5396 | 25.0396 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-25 | 22.7625 | 22.046 | 24.0429 | 24.5 | 25 | 25.5 | 24.5429 | 25.0429 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-26 | 22.4792 | 22.0303 | 24.0385 | 24.5 | 25 | 25.5 | 24.5385 | 25.0385 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-27 | 20.8333 | 22.0031 | 24.0309 | 24.5 | 25 | 25.5 | 24.5309 | 25.0309 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-28 | 20.4542 | 21.9076 | 24.0041 | 24.5 | 25 | 25.5 | 24.5041 | 25.0041 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-29 | 21.1125 | 21.8194 | 23.9794 | 24.5 | 25 | 25.5 | 24.4794 | 24.9794 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-30 | 21.1167 | 21.7857 | 23.97 | 24.5 | 25 | 25.5 | 24.47 | 24.97 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1990-12-31 | 21.1792 | 21.7544 | 23.9612 | 24.5 | 25 | 25.5 | 24.4612 | 24.9612 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## Summary
Adaptive comfort degree days (ACDD)
| Baseline | IMAC | Plant_SI | IMAC+Plant_S1 | Plant_S2 | IMAC+Plant_S2
Kota | 1442.3 | 1014.0791 | 1322.9708 | 898.2832 | 1209.1417 | 789.1
Gwalior | 1323.7917 | 940.1656 | 1219.025 | 839.6666 | 1116.6333 | 743.3735
Pilani | 1228.2792 | 875.6863 | 1118.45 | 774.2798 | 1010.3833 | 678.2748
New Delhi | 1175.5208 | 833.0949 | 1075.5583 | 732.5154 | 978.1083 | 634.7236
Hyderabad | 988.3583 | 688.0245 | 863.9292 | 577.1638 | 749.8375 | 479.1277

## %EnergySaving
Adaptive cooilng degree days (ACDD)
Cities | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6
Hyderabad | 988.3583 | 688.0245 | 863.9292 | 577.1638 | 749.8375 | 479.1277
Delhi | 1175.5208 | 833.0949 | 1075.5583 | 732.5154 | 978.1083 | 634.7236 | 540.7972 | 198.3712
Pilani | 1228.2792 | 875.6863 | 1118.45 | 774.2798 | 1010.3833 | 678.2748 | 0.46005 | 0.23811
Gwalior | 1323.7917 | 940.1656 | 1219.025 | 839.6666 | 1116.6333 | 743.3735
Kota | 1442.3 | 1014.0791 | 1322.9708 | 898.2832 | 1209.1417 | 789.1
| Baseline | IMAC | Plant_SI | IMAC+Plant_S1 | Plant_S2 | IMAC+Plant_S2
Hyderabad |  | 30.39% | 12.59% | 41.6% | 24.13% | 51.52% |  | 42
Delhi |  | 29.13% | 8.504% | 37.69% | 16.79% | 46% |  | 38
Pilani |  | 28.71% | 8.942% | 36.96% | 17.74% | 44.78% |  | 37
Gwalior |  | 28.98% | 7.914% | 36.57% | 15.65% | 43.85% |  | 37
Kota |  | 29.69% | 8.274% | 37.72% | 16.17% | 45.29% |  | 38
Percentage cooling energy saving for different scenario considering PMV as baseline
| Cities | PMV+ 0.5°C | PMV+ 1.0°C | IMAC | IMAC + 0.5°C
| Hyderabad | 13 | 24 | 30 | 42
| Delhi | 9 | 17 | 29 | 38
| Pilani | 9 | 18 | 29 | 37
| Gwalior | 8 | 16 | 29 | 37
| Kota | 8 | 16 | 30 | 38

## Plot
Adaptive cooilng degree days (ACDD)
Cities | PMV Baseline | PMV+ 0.5°C | PMV+ 1.0°C | IMAC | IMAC + 0.5°C
Kota | 1442.3 | 1322.9708 | 1209.1417 | 1014.0791 | 898.2832
Gwalior | 1323.7917 | 1219.025 | 1116.6333 | 940.1656 | 839.6666
Pilani | 1228.2792 | 1118.45 | 1010.3833 | 875.6863 | 774.2798
New Delhi | 1175.5208 | 1075.5583 | 978.1083 | 833.0949 | 732.5154
Hyderabad | 988.3583 | 863.9292 | 749.8375 | 688.0245 | 577.1638